## HZI825-RS485
MODBUS COMMUNICATION ADDRESS AND DESIGNATION DETAILS
All communication addresses, except communication parameters (4) are read only RO (read function 03/04).
The communication protocol adopts the standard MODBUS-RTU protocol, with master-slave acknowledgment connection (half duplex).
As standard the baud rate is set to 38400, parity bit to 1 (these settings can be modified through Modbus). When the product is communicating the COM Led will blink.
1. Input / Output state
Dec. Address | Word count | Description | Unit
10008 | 1 | Position I input state (70-71) | 0 : OFF
1 : ON
10009 | 1 | Position II input state (70-72) | 0 : OFF
1 : ON
10010 | 1 | Position 0 input state (70-73) | 0 : OFF
1 : ON
10011 | 1 | Fire Input state (F1-F2) | 0 : OFF
1 : ON
10012 | 1 | CTRL inhibit (63A-64A) | 0 : Automatic
1 : Inhibit
10022 | 1 | Genset control output (51-52-54) | 0 : Genset start order OFF
1 : Genset start order ON
10024 | 1 | Control signal output 0 (16-17) | 0 : Output not activated
1 : Output activated
10025 | 1 | Control signal output I (15-17) | 0 : Output not activated
1 : Output activated
10026 | 1 | Control signal output II (14-17) | 0 : Output not activated
1 : Output activated
2. Status
Dec. Address | Word count | Description | Unit
10124 | 1 | Source 1 power status | 0 : OFF
1 : ON
10125 | 1 | Source 2 power status | 0 : OFF
1 : ON
10040 … 10071 | 32 | Alarms 01 … 32 | 0 : No alarm
1 : Alarm
40005 | 1 | HZI825 operating mode | 2 : Manual
3 : Automatic
4 : Test
3. Voltage sensing
Dec. Address | Word count | Description | Unit
10192 | 1 | Source 1 L1-N voltage value | (V)
10193 | 1 | Source 1 L2-N voltage value | (V)
10194 | 1 | Source 1 L3-N voltage value | (V)
10195 | 1 | Source 1 L-N average voltage | (V)
10196 | 1 | Source 1 L1 –L2 voltage value | (V)
10197 | 1 | Source 1 L2 –L3 voltage value | (V)
10198 | 1 | Source 1 L3 –L1 voltage value | (V)
10199 | 1 | Source 1 L-L average voltage | (V)
10204 | 1 | Source 1 frequency | (0.1 Hz)
10205 | 1 | Source 2 L1-N voltage value | (V)
10206 | 1 | Source 2 L2-N voltage value | (V)
10207 | 1 | Source 2 L3-N voltage value | (V)
10208 | 1 | Source 2 L-N average voltage | (V)
10209 | 1 | Source 2 L1 –L2 voltage value | (V)
10210 | 1 | Source 2 L2 –L3 voltage value | (V)
10211 | 1 | Source 2 L3 –L1 voltage value | (V)
10212 | 1 | Source 2 L-L average voltage | (V)
10217 | 1 | Source 2 frequency | (0.1 Hz)
4. Communication parameters
Dec. Address | Word count | Description | Unit
40017 | 1 | HZI825 communication node address | 1 … 247
40018 | 1 | Baud rate | 2 : 2 400
3 : 4 800
4 : 9 600
5 : 19 200
6 : 38 400
40019 | 1 | Serial Data format | 1 : 8N
2 : 80
3 : 8E
4 : 70
5 : 7E
40020 | 1 | Stop bit | 1 … 2
As standard the baud rate is set to 38 400, parity bit to 1, Modbus address 3 these parameters can be changed using the write function 10.
Once the configuration is done, write data 1 at address Dec. 40565. After changing the parameters the product buzzer will sound twice and the Com LED will stay on.
To reset to default parameters press the RES button for 30 seconds, the product will reboot and the standard communication settings will be set.
5. Maintenance
Dec. Address | Word count | Description | Unit
10126 | 2 | Position I operation count in AUTO mode | 0 … 60 000
10128 | 2 | Position II operation count in AUTO mode | 0 … 60 000
10130 | 2 | Position I operation count in Manual mode | 0 … 60 000
10132 | 2 | Position II operation count in Manual mode | 0 … 60 000
10170 … 10179 | 8 | Serial number | (V)
10186 | 1 | Hardware version | (V)
10187 | 1 | Software version | (V)