## HZI855-RS485
Product Identification
Product information
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 50005 | 0xC355 | 1 | Product ID (EX: 1000 ATS3) | - | U16 | Info | NONE | READ | READ
| 50006 | 0xC356 | 1 | MODBUS Table Version | - | U16 | Info | NONE | READ | READ
| 50007 | 0xC357 | 1 | Product software version (EX: 100 Version 1.00) | - | U16 | Info | NONE | READ | READ
| 50008 | 0xC358 | 1 | Serial_AA_SS | - | U16_HEX | Info | NONE | READ | READ
| 50009 | 0xC359 | 1 | Serial_SST_L | - | U16_HEX | Info | NONE | READ | READ
| 50010 | 0xC35A | 1 | Serial_order | - | U16 | Info | NONE | READ | READ
| 50011 | 0xC35B | 2 | Serial_Reserve | - | U32 | Info | NONE | READ | READ
| 50013 | 0xC35D | 4 | See "Code table" tab for more details | - | U64_HEX | Info | NONE | READ | READ
| 50017 | 0xC361 | 1 | Customization data loaded (True/False) | - | U8 | Info | NONE | READ | READ
| 50018 | 0xC362 | 1 | Product version (Major) | - | U16 | Info | NONE | READ | READ
| 50019 | 0xC363 | 1 | Product version (Minor) | - | U16 | Info | NONE | READ | READ
| 50020 | 0xC364 | 1 | Product version (Revision) | - | U16 | Info | NONE | READ | READ
| 50021 | 0xC365 | 1 | Product version (Build) | - | U16 | Info | NONE | READ | READ
| 50022 | 0xC366 | 3 | Product build date | - | DATETIME_3 | Info | NONE | READ | READ
| 50025 | 0xC369 | 1 | Software technical base version (Major) | - | U16 | Info | NONE | READ | READ
| 50026 | 0xC36A | 1 | Software technical base version (Minor) | - | U16 | Info | NONE | READ | READ
| 50027 | 0xC36B | 1 | Software technical base version (Revision) | - | U16 | Info | NONE | READ | READ
| 50028 | 0xC36C | 1 | Customization version (Major) | - | U16 | Info | NONE | READ | READ
| 50029 | 0xC36D | 1 | Customization version (Minor) | - | U16 | Info | NONE | READ | READ
| 50030 | 0xC36E | 4 | Product VLO (EX : "880100") | - | STRING_NORM | Info | NONE | READ | READ
| 50034 | 0xC372 | 4 | Customization VLO (EX : "880700") | - | STRING_NORM | Info | NONE | READ | READ
| 50038 | 0xC376 | 4 | Software technical base VLO (EX : "880600") | - | STRING_NORM | Info | NONE | READ | READ
| 50042 | 0xC37A | 8 | Vendor name (EX : "HAGER") | - | STRING_NORM | Info | NONE | READ | READ
| 50050 | 0xC382 | 8 | Product name (EX : "HZI855") | - | STRING_NORM | Info | NONE | READ | READ
| 50058 | 0xC38A | 8 | Extended name | - | STRING_NORM | Info | NONE | READ | READ
| 50066 | 0xC392 | 1 | Resource version (Build 2) | - | U16 | Info | NONE | READ | READ
| 50067 | 0xC393 | 2 | Net ID | - | U32_HEX | Info | NONE | READ | READ
Identification by blinking LED
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57864 | 0xE208 | 1 | Action | - | U16 | Commands | NONE | WRITE | WRITE
1 : Start blinking
Visualization
ATS Status
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 20480 | 0x5000 | 2 | Date & Time Current | - | DATETIME | Info | NONE | READ | READ
| 20482 | 0x5002 | 1 | Operating Mode | - | U16_HEX | Info | NONE | READ | READ
0x0010 : Auto Mode
0x0020 : Manu Mode
0x0040 : Inhibit Mode
0x0080 : Partial Inhibit Mode
| 20483 | 0x5003 | 1 | Switch Position | - | U8 | Info | NONE | READ | READ
0 : Unknown
1 : Position 0
2 : Position 1
3 : Position 2
| 20484 | 0x5004 | 1 | Source 1 Start Generator relay State | - | U8 | Info | NONE | READ | READ
0 : Not active
1 : Active
| 20485 | 0x5005 | 1 | Source 2 Start Generator relay State | - | U8 | Info | NONE | READ | READ
0 : Not Active
1 : Active
| 20486 | 0x5006 | 1 | Priority | - | U8 | Info | NONE | READ | READ
0 : Network
1 : Source 1
2 : Source 2
| 20487 | 0x5007 | 1 | Source1 State | - | U8 | Info | NONE | READ | READ
0 : Under Threshold BusBar
1 : Present
2 : Available
| 20488 | 0x5008 | 1 | Source2 State | - | U8 | Info | NONE | READ | READ
0 : Under Threshold BusBar
1 : Present
2 : Available
| 20489 | 0x5009 | 1 | Test in progress | - | U16_HEX | Info | NONE | READ | READ
0x0000 : None
0x0001 : TOF
0x0002 : EOF
0x0004 : TON
0x0008 : EON
| 20490 | 0x500A | 1 | Alarm / Fault summary | - | U8 | Info | NONE | READ | READ
0 : None
1 : Alarm
2 : Fault
3 : Alarm + Fault
| 20491 | 0x500B | 1 | Active Fault (with highest priority) | - | U16 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 20492 | 0x500C | 1 | Last Switch over cause | - | U8 | Info | NONE | READ | READ
0 : None
1 : Manual
2 : Remote controlled
3 : Under voltage source 1
4 : Under voltage source 2
5 : Over voltage source 1
6 : Over voltage source 2
7 : Under Frequence source 1
8 : Under Frequence source 2
9 : Over Frequence source 1
10 : Over Frequence source 2
11 : Unbalance Source 1
12 : Unbalance Source 2
13 : Rotation Source 1
14 : Rotation Source 2
| 20493 | 0x500D | 1 | Product is available | - | U8 | Info | NONE | READ | READ
0 : Not available
1 : Available
| 20494 | 0x500E | 1 | Source Inhibition state | - | U8 | Info | NONE | READ | READ
0 : No inhibition
1 : S1 Inhibited
2 : S2 Inhibited
3 : Both source inhibited
Timer state
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 21248 | 0x5300 | 2 | Date & Time Current | s | DATETIME | Info | NONE | READ | READ
| 21250 | 0x5302 | 1 | 1FT Source1 Failure Timer | s 10⁻¹ | U16 | Info | NONE | READ | READ
| 21251 | 0x5303 | 1 | 1RT Source1 Available/Return Timer | s | U16 | Info | NONE | READ | READ
| 21252 | 0x5304 | 1 | 1CT Source1 Genset Cooldown timer | s | U16 | Info | NONE | READ | READ
| 21253 | 0x5305 | 1 | 10T Source1 return to 0 timer | s | U16 | Info | NONE | READ | READ
| 21254 | 0x5306 | 1 | 1ST Source1 Start TimeOut timer | s | U16 | Info | NONE | READ | READ
| 21255 | 0x5307 | 1 | 2FT Source2 Failure Timer | s 10⁻¹ | U16 | Info | NONE | READ | READ
| 21256 | 0x5308 | 1 | 2RT Source2 Available/Return Timer | s | U16 | Info | NONE | READ | READ
| 21257 | 0x5309 | 1 | 2CT Source2 Genset Cooldown timer | s | U16 | Info | NONE | READ | READ
| 21258 | 0x530A | 1 | 20T Source2 return to 0 timer | s | U16 | Info | NONE | READ | READ
| 21259 | 0x530B | 1 | 2ST Source2 Start TimeOut timer | s | U16 | Info | NONE | READ | READ
| 21260 | 0x530C | 1 | DBT Dead Band timer | s | U16 | Info | NONE | READ | READ
| 21261 | 0x530D | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21262 | 0x530E | 1 | Limit_TOT Test on load is limited | - | U8 | Info | NONE | READ | READ
0 : unlimited
1 : limited
| 21263 | 0x530F | 1 | TOT Test on load duration timer | s | U16 | Info | NONE | READ | READ
| 21264 | 0x5310 | 1 | T3T Test on load end timer | s | U16 | Info | NONE | READ | READ
| 21265 | 0x5311 | 1 | Limit_TFT Test off load is limited | - | U8 | Info | NONE | READ | READ
0 : unlimited
1 : limited
| 21266 | 0x5312 | 1 | TFT Test off load duration timer | s | U16 | Info | NONE | READ | READ
| 21267 | 0x5313 | 1 | E1T Time before external order on load | s | U16 | Info | NONE | READ | READ
| 21268 | 0x5314 | 1 | E3T Time after external order on load | s | U16 | Info | NONE | READ | READ
| 21269 | 0x5315 | 1 | Limit_E2T External order on load is limited | - | U8 | Info | NONE | READ | READ
0 : unlimited
1 : limited
| 21270 | 0x5316 | 1 | E2T External order on load duration | s | U16 | Info | NONE | READ | READ
| 21271 | 0x5317 | 1 | E5T Time before external order off load | s | U16 | Info | NONE | READ | READ
| 21272 | 0x5318 | 1 | E7T Time after external order off load | s | U16 | Info | NONE | READ | READ
| 21273 | 0x5319 | 1 | Limit_E6T External order off load is limited | - | U8 | Info | NONE | READ | READ
0 : unlimited
1 : limited
| 21274 | 0x531A | 1 | E6T External order off load duration | s | U16 | Info | NONE | READ | READ
| 21275 | 0x531B | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21276 | 0x531C | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21277 | 0x531D | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21278 | 0x531E | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21279 | 0x531F | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21280 | 0x5320 | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21281 | 0x5321 | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21282 | 0x5322 | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21283 | 0x5323 | 1 | Reserved | - | - | Info | NONE | READ | READ
| 21284 | 0x5324 | 1 | OD1: On Delay 1 Timer | s | U16 | Info | NONE | READ | READ
| 21285 | 0x5325 | 1 | OD2: On Delay 2 Timer | s | U16 | Info | NONE | READ | READ
| 21286 | 0x5326 | 1 | OD3: On Delay 3 Timer | s | U16 | Info | NONE | READ | READ
| 21287 | 0x5327 | 1 | CH1: Charging time for breaker 1 | s 10⁻¹ | U16 | Info | NONE | READ | READ
| 21288 | 0x5328 | 1 | CH2: Charging time for breaker 2 | s 10⁻¹ | U16 | Info | NONE | READ | READ
| 21289 | 0x5329 | 2 | 1CY: Source 1 Cycler Duration | s | U32 | Info | NONE | READ | READ
| 21291 | 0x532B | 2 | 2CY: Source 2 Cycler Duration | s | U32 | Info | NONE | READ | READ
| 21293 | 0x532D | 1 | PreODx : On Delay pre-transfer timer | s | U16 | Info | NONE | READ | READ
Measure
Network Inst Source #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 36864 | 0x9000 | 2 | Date of last instance | s | DATETIME | Info | NONE | READ | READ
| 36866 | 0x9002 | 1 | Integration time | s / 5 | U16 | Info | NONE | READ | READ
| 36867 | 0x9003 | 2 | System Ph-N Voltage | V 10⁻² | U32 | Info | NONE | READ | READ
| 36869 | 0x9005 | 2 | System Ph-Ph Voltage | V 10⁻² | U32 | Info | NONE | READ | READ
| 36871 | 0x9007 | 2 | Frequency | mHz | U32 | Info | NONE | READ | READ
| 36873 | 0x9009 | 2 | Ph-N Voltage : V1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36875 | 0x900B | 2 | Ph-N Voltage : V2 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36877 | 0x900D | 2 | Ph-N Voltage : V3 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36879 | 0x900F | 2 | Ph-N Voltage : Vn | V 10⁻² | U32 | Info | NONE | READ | READ
| 36881 | 0x9011 | 2 | Ph-Ph Voltage : U12 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36883 | 0x9013 | 2 | Ph-Ph Voltage : U23 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36885 | 0x9015 | 2 | Ph-Ph Voltage : U31 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36887 | 0x9017 | 2 | Vdir | V 10⁻² | U32 | Info | NONE | READ | READ
| 36889 | 0x9019 | 2 | Vinv | V 10⁻² | U32 | Info | NONE | READ | READ
| 36891 | 0x901B | 2 | Vhom | V 10⁻² | U32 | Info | NONE | READ | READ
| 36893 | 0x901D | 1 | Vnb | % / 100 | U16 | Info | NONE | READ | READ
| 36894 | 0x901E | 2 | Udir | V 10⁻² | U32 | Info | NONE | READ | READ
| 36896 | 0x9020 | 2 | Uinv | V 10⁻² | U32 | Info | NONE | READ | READ
| 36898 | 0x9022 | 1 | Unb | % / 100 | U16 | Info | NONE | READ | READ
| 36899 | 0x9023 | 1 | Vnba | % / 100 | U16 | Info | NONE | READ | READ
| 36900 | 0x9024 | 1 | Unba | % / 100 | U16 | Info | NONE | READ | READ
Network Inst Source #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 36908 | 0x902C | 2 | Date of last instance | s | DATETIME | Info | NONE | READ | READ
| 36910 | 0x902E | 1 | Integration time | s / 5 | U16 | Info | NONE | READ | READ
| 36911 | 0x902F | 2 | System Ph-N Voltage | V 10⁻² | U32 | Info | NONE | READ | READ
| 36913 | 0x9031 | 2 | System Ph-Ph Voltage | V 10⁻² | U32 | Info | NONE | READ | READ
| 36915 | 0x9033 | 2 | Frequency | mHz | U32 | Info | NONE | READ | READ
| 36917 | 0x9035 | 2 | Ph-N Voltage : V1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36919 | 0x9037 | 2 | Ph-N Voltage : V2 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36921 | 0x9039 | 2 | Ph-N Voltage : V3 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36923 | 0x903B | 2 | Ph-N Voltage : Vn | V 10⁻² | U32 | Info | NONE | READ | READ
| 36925 | 0x903D | 2 | Ph-Ph Voltage : U12 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36927 | 0x903F | 2 | Ph-Ph Voltage : U23 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36929 | 0x9041 | 2 | Ph-Ph Voltage : U31 | V 10⁻² | U32 | Info | NONE | READ | READ
| 36931 | 0x9043 | 2 | Vdir | V 10⁻² | U32 | Info | NONE | READ | READ
| 36933 | 0x9045 | 2 | Vinv | V 10⁻² | U32 | Info | NONE | READ | READ
| 36935 | 0x9047 | 2 | Vhom | V 10⁻² | U32 | Info | NONE | READ | READ
| 36937 | 0x9049 | 1 | Vnb | % / 100 | U16 | Info | NONE | READ | READ
| 36938 | 0x904A | 2 | Udir | V 10⁻² | U32 | Info | NONE | READ | READ
| 36940 | 0x904C | 2 | Uinv | V 10⁻² | U32 | Info | NONE | READ | READ
| 36942 | 0x904E | 1 | Unb | % / 100 | U16 | Info | NONE | READ | READ
| 36943 | 0x904F | 1 | Vnba | % / 100 | U16 | Info | NONE | READ | READ
| 36944 | 0x9050 | 1 | Unba | % / 100 | U16 | Info | NONE | READ | READ
Network Inst. Fundamental Source #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 37120 | 0x9100 | 2 | Date of last instance | s | DATETIME | Info | NONE | READ | READ
| 37122 | 0x9102 | 1 | Integration time | s / 5 | U16 | Info | NONE | READ | READ
| 37123 | 0x9103 | 2 | Ph-N voltage: V1h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37125 | 0x9105 | 2 | Ph-N voltage: V2h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37127 | 0x9107 | 2 | Ph-N voltage: V3h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37129 | 0x9109 | 2 | Ph-N voltage: Vnh1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37131 | 0x910B | 1 | Ph-N voltage phase: phV1h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37132 | 0x910C | 1 | Ph-N voltage phase: phV2h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37133 | 0x910D | 1 | Ph-N voltage phase: phV3h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37134 | 0x910E | 1 | Ph-N voltage phase: phVnh1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37135 | 0x910F | 2 | Ph-Ph voltage: U12h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37137 | 0x9111 | 2 | Ph-Ph voltage: U23h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37139 | 0x9113 | 2 | Ph-Ph voltage: U31h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37141 | 0x9115 | 1 | Ph-Ph voltage phase: phU12h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37142 | 0x9116 | 1 | Ph-Ph voltage phase: phU23h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37143 | 0x9117 | 1 | Ph-Ph voltage phase: phU31h1 | ? / 10 | S16 | Info | NONE | READ | READ
Network Inst. Fundamental Source #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 37296 | 0x91B0 | 2 | Date of last instance | s | DATETIME | Info | NONE | READ | READ
| 37298 | 0x91B2 | 1 | Integration time | s / 5 | U16 | Info | NONE | READ | READ
| 37299 | 0x91B3 | 2 | Ph-N voltage: V1h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37301 | 0x91B5 | 2 | Ph-N voltage: V2h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37303 | 0x91B7 | 2 | Ph-N voltage: V3h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37305 | 0x91B9 | 2 | Ph-N voltage: Vnh1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37307 | 0x91BB | 1 | Ph-N voltage phase: phV1h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37308 | 0x91BC | 1 | Ph-N voltage phase: phV2h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37309 | 0x91BD | 1 | Ph-N voltage phase: phV3h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37310 | 0x91BE | 1 | Ph-N voltage phase: phVnh1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37311 | 0x91BF | 2 | Ph-Ph voltage: U12h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37313 | 0x91C1 | 2 | Ph-Ph voltage: U23h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37315 | 0x91C3 | 2 | Ph-Ph voltage: U31h1 | V 10⁻² | U32 | Info | NONE | READ | READ
| 37317 | 0x91C5 | 1 | Ph-Ph voltage phase: phU12h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37318 | 0x91C6 | 1 | Ph-Ph voltage phase: phU23h1 | ? / 10 | S16 | Info | NONE | READ | READ
| 37319 | 0x91C7 | 1 | Ph-Ph voltage phase: phU31h1 | ? / 10 | S16 | Info | NONE | READ | READ
Inputs / Outputs
Logical Input #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11520 | 0x2D00 | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11521 | 0x2D01 | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Input #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11522 | 0x2D02 | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11523 | 0x2D03 | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Input #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11524 | 0x2D04 | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11525 | 0x2D05 | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Input #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11526 | 0x2D06 | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11527 | 0x2D07 | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Input #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11528 | 0x2D08 | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11529 | 0x2D09 | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Input #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11530 | 0x2D0A | 1 | Input function | - | U8 | Info | NONE | READ | READ
0 : --- - None
4 : ALO - Alarm Logical In
5 : AACK - Alarm Aknoledge
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
120 : MS1 - BypassMTS MTS I
121 : MS0 - BypassMTS MTS 0
122 : MS2 - BypassMTS MTS II
123 : CON - BypassMTS Connected
124 : WTH - BypassMTS Withdrawn
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
255 : eFctMultiple
| 11531 | 0x2D0B | 1 | Input State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Inputs All
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11248 | 0x2BF0 | 1 | Inputs number | - | U16 | Info | NONE | READ | READ
| 11249 | 0x2BF1 | 2 | Bit x : Input x Available (1)/Not available (0) | - | U32_HEX | Info | NONE | READ | READ
| 11251 | 0x2BF3 | 2 | Bit x : Input x Activated (1)/Deactivated (0) | - | U32_HEX | Info | NONE | READ | READ
| 11253 | 0x2BF5 | 2 | Bit x : Input x NC (1)/NO (0) | - | U32_HEX | Info | NONE | READ | READ
Logical Output (start gen) #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11600 | 0x2D50 | 1 | Output function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
75 : GS1 - Genset Source 1 start
76 : GS2 - Genset Source 2 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 11601 | 0x2D51 | 1 | Output State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Output (start gen) #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11616 | 0x2D60 | 1 | Output function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
75 : GS1 - Genset Source 1 start
76 : GS2 - Genset Source 2 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 11617 | 0x2D61 | 1 | Output State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Output (start gen) #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11632 | 0x2D70 | 1 | Output function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
75 : GS1 - Genset Source 1 start
76 : GS2 - Genset Source 2 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 11633 | 0x2D71 | 1 | Output State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Output (start gen) #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11648 | 0x2D80 | 1 | Output function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
75 : GS1 - Genset Source 1 start
76 : GS2 - Genset Source 2 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 11649 | 0x2D81 | 1 | Output State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Logical Outputs All
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11280 | 0x2C10 | 1 | Outputs number | - | U16 | Info | NONE | READ | READ
| 11281 | 0x2C11 | 2 | Bit x : Output x Available (1)/Not available (0) | - | U32_HEX | Info | NONE | READ | READ
| 11283 | 0x2C13 | 2 | Bit x : Output x Activated (1)/Deactivated (0) | - | U32_HEX | Info | NONE | READ | READ
| 11285 | 0x2C15 | 2 | Bit x : Output x NC (1)/NO (0) | - | U32_HEX | Info | NONE | READ | READ
Relay informations #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 16464 | 0x4050 | 1 | Output Relay function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 16465 | 0x4051 | 1 | Output Relay State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Relay informations #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 16472 | 0x4058 | 1 | Output Relay function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 16473 | 0x4059 | 1 | Output Relay State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Relay informations #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 16480 | 0x4060 | 1 | Output Relay function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 16481 | 0x4061 | 1 | Output Relay State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Relay informations #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 16488 | 0x4068 | 1 | Output Relay function | - | U8 | Info | NONE | READ | READ
0 : --- - None
6 : ARO - Alarm Report Output
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
111 : PRL - ATyS Bypass PARALELLING
112 : TST - ATyS Bypass TEST
113 : EMG - ATyS Bypass EMERGENCY BYPASS
114 : NRM - ATyS Bypass NORMAL BYPASS
133 : OD1 - On Delay 1 Timer
134 : OD2 - On Delay 2 Timer
135 : OD3 - On Delay 3 Timer
255 : eFctMultiple
| 16481 | 0x4069 | 1 | Output Relay State | - | U8 | Info | NONE | READ | READ
0 : Deactivated
1 : Activated
Statistics
Operating hours meters
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 512 | 0x0200 | 2 | Total operating hours counter | s | U32 | Info | NONE | READ | READ
| 514 | 0x0202 | 2 | Partial operating hours counter | s | U32 | Info | NONE | READ | READ
Product Time meters
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 23296 | 0x5B00 | 2 | Total time in position 1 | s | U32 | Info | NONE | READ | READ
| 23298 | 0x5B02 | 2 | User partial time in position 1 | s | U32 | Info | NONE | READ | READ
| 23300 | 0x5B04 | 2 | Time in position 1 since last commutation | s | U32 | Info | NONE | READ | READ
| 23302 | 0x5B06 | 2 | Total time load supplied by source 1 | s | U32 | Info | NONE | READ | READ
| 23304 | 0x5B08 | 2 | Total time in position 2 | s | U32 | Info | NONE | READ | READ
| 23306 | 0x5B0A | 2 | User partial time in position 2 | s | U32 | Info | NONE | READ | READ
| 23308 | 0x5B0C | 2 | Time in position 2 since last commutation | s | U32 | Info | NONE | READ | READ
| 23310 | 0x5B0E | 2 | Total time load supplied by source 2 | s | U32 | Info | NONE | READ | READ
| 23312 | 0x5B10 | 2 | Start order active duration Genset source 1 | s | U32 | Info | NONE | READ | READ
| 23314 | 0x5B12 | 2 | Start order active duration Genset source 2 | s | U32 | Info | NONE | READ | READ
| 23316 | 0x5B14 | 1 | Start order activation counter Genset source 1 | - | U16 | Info | NONE | READ | READ
| 23317 | 0x5B15 | 1 | Start order activation counter Genset source 2 | - | U16 | Info | NONE | READ | READ
| 23318 | 0x5B16 | 2 | Engine Run Time Source 1 | h | U32 | Info | NONE | READ | READ
| 23320 | 0x5B18 | 2 | Engine Run Time - On Load - Source 1 | h | U32 | Info | NONE | READ | READ
| 23322 | 0x5B1A | 2 | Engine Run Time Source 2 | h | U32 | Info | NONE | READ | READ
| 23324 | 0x5B1C | 2 | Engine Run Time - On Load - Source 2 | h | U32 | Info | NONE | READ | READ
Switch counters
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 23552 | 0x5C00 | 2 | Switch Operating hours counter | s | U32 | Info | NONE | READ | READ
| 23554 | 0x5C02 | 1 | Total Cycles counter | - | U16 | Info | NONE | READ | READ
| 23555 | 0x5C03 | 1 | Cycles in auto mode | - | U16 | Info | NONE | READ | READ
| 23556 | 0x5C04 | 1 | Cycles in remote control mode | - | U16 | Info | NONE | READ | READ
| 23557 | 0x5C05 | 1 | Total switches counter | - | U16 | Info | NONE | READ | READ
| 23558 | 0x5C06 | 1 | Total Position 0 switches counter | - | U16 | Info | NONE | READ | READ
| 23559 | 0x5C07 | 1 | Total Position 1 switches counter | - | U16 | Info | NONE | READ | READ
| 23560 | 0x5C08 | 1 | Total Position 2 switches counter | - | U16 | Info | NONE | READ | READ
| 23561 | 0x5C09 | 1 | Position 0 switches in auto mode counter | - | U16 | Info | NONE | READ | READ
| 23562 | 0x5C0A | 1 | Position 1 switches in auto mode counter | - | U16 | Info | NONE | READ | READ
| 23563 | 0x5C0B | 1 | Position 2 switches in auto mode counter | - | U16 | Info | NONE | READ | READ
| 23564 | 0x5C0C | 1 | Position 0 switches in control mode counter | - | U16 | Info | NONE | READ | READ
| 23565 | 0x5C0D | 1 | Position 1 switches in control mode counter | - | U16 | Info | NONE | READ | READ
| 23566 | 0x5C0E | 1 | Position 2 switches in control mode counter | - | U16 | Info | NONE | READ | READ
Breaker counters
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 23760 | 0x5CD0 | 2 | Date of last Trip breaker 1 | s | DATETIME | Info | NONE | READ | READ
| 23762 | 0x5CD2 | 2 | Date of last Trip breaker 2 | s | DATETIME | Info | NONE | READ | READ
| 23764 | 0x5CD4 | 1 | Number of trip breaker 1 (activation of TP1) | - | U16 | Info | NONE | READ | READ
| 23765 | 0x5CD5 | 1 | Number of trip breaker 2 (activation of TP2) | - | U16 | Info | NONE | READ | READ
Diagnostic
Source NetCnx computed #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 12320 | 0x3020 | 1 | Computed : Network connection type | - | U8 | Info | NONE | READ | READ
0 : Not computed
1 : 1P + N
2 : 2P
3 : 2P + N
4 : 3P
5 : 3P + N
| 12321 | 0x3021 | 2 | Computed : Nominal Voltage | V | U32 | Info | NONE | READ | READ
| 12323 | 0x3023 | 1 | Computed : Nominal Frequency | - | U8 | Info | NONE | READ | READ
0 : 50 Hz - eDefFnom_50Hz
1 : 60 Hz - eDefFnom_60Hz
2 : NU - Error
| 12324 | 0x3024 | 1 | Computed : Phase rotation | - | U8 | Info | NONE | READ | READ
0 : V1 - V2 - V3
1 : V1 - V3 - V2
| 12325 | 0x3025 | 1 | Diagnosticated : Network connection type | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12326 | 0x3026 | 1 | Diagnosticated : Nominal Voltage | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12327 | 0x3027 | 1 | Diagnosticated : Nominal Frequency | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12328 | 0x3028 | 1 | Diagnosticated : Phase rotation | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
Source NetCnx computed #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 12330 | 0x302A | 1 | Computed : Network connection type | - | U8 | Info | NONE | READ | READ
0 : Not computed
1 : 1P + N
2 : 2P
3 : 2P + N
4 : 3P
5 : 3P + N
| 12331 | 0x302B | 2 | Computed : Nominal Voltage | V | U32 | Info | NONE | READ | READ
| 12333 | 0x302D | 1 | Computed : Nominal Frequency | - | U8 | Info | NONE | READ | READ
0 : 50 Hz - eDefFnom_50Hz
1 : 60 Hz - eDefFnom_60Hz
2 : NU - Error
| 12334 | 0x302E | 1 | Computed : Phase rotation | - | U8 | Info | NONE | READ | READ
0 : V1 - V2 - V3
1 : V1 - V3 - V2
| 12335 | 0x302F | 1 | Diagnosticated : Network connection type | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12336 | 0x3030 | 1 | Diagnosticated : Nominal Voltage | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12337 | 0x3031 | 1 | Diagnosticated : Nominal Frequency | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
| 12338 | 0x3032 | 1 | Diagnosticated : Phase rotation | - | U8 | Info | NONE | READ | READ
0 : Not Diagnosticated
1 : NOK
2 : OK
Modbus diag
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 880 | 0x0370 | 2 | RS SlaveRxRequestCnt | - | U32 | Info | NONE | READ | READ
| 882 | 0x0372 | 2 | RS SlaveTxRequestCnt | - | U32 | Info | NONE | READ | READ
| 884 | 0x0374 | 2 | RS SlaveErrorCnt | - | U32 | Info | NONE | READ | READ
Modbus diag
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 879 | 0x036F | 1 | Modbus diag reset | - | U16 | Commands | USER | NONE | WRITE
0 : No action
1 : Reset statistics
Events Log
Command
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4720 | 0x1270 | 1 | Start record number (0 to 65534) or 65535 for last record | - | U16 | Command | NONE | WRITE_MANY | WRITE_MANY
Header
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4736 | 0x1280 | 1 | Next record number | - | U16 | Header | NONE | READ | READ
| 4737 | 0x1281 | 1 | Items count (max 3 per request) | - | U16 | Header | NONE | READ | READ
| 4738 | 0x1282 | 1 | Item size (words) | - | U16 | Header | NONE | READ | READ
Data
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4739 | 0x1283 | 1 | Event ID | - | U16_HEX | Data | NONE | READ | READ
0x1102 : BET in default
0x1103 : BET not present
0x1105 : StartGen relay fault
0x1106 : Internal Diag
0x1107 : ADC Reference Fault
0x2001 : Source 1 Lost
0x2002 : Source 1 comes back
0x2003 : Source 1 not started (1ST / 2ST)
0x2004 : Source 1 Undervoltage
0x2005 : Source 1 Overvoltage
0x2006 : Source 1 Unbalanced
0x2007 : Source 1 Underfrequency
0x2008 : Source 1 Overfrequency
0x2009 : Source 1 Rotation fault
0x200A : Source 1 Neutral fault
0x200B : External fault with zero return source 1
0x200C : External fault without zero return source 1
0x200D : Source 1 Overload
0x200E : Source 1 Inhibit Start
0x200F : Source 1 Inhibit Stop
0x2101 : Source 2 Lost
0x2102 : Source 2 comes back
0x2103 : Source 2 not started (1ST / 2ST)
0x2104 : Source 2 Undervoltage
0x2105 : Source 2 Overvoltage
0x2106 : Source 2 Unbalanced
0x2107 : Source 2 Underfrequency
0x2108 : Source 2 Overfrequency
0x2109 : Source 2 Rotation fault
0x210A : Source 2 Neutral fault
0x210B : External fault with zero return source 2
0x210C : External fault without zero return source 2
0x210D : Source 2 Overload
0x210E : Source 2 Inhibit Start
0x210F : Source 2 Inhibit Stop
0x2201 : Test on load start
0x2202 : Test on load end
0x2203 : Test on load failed
0x2204 : Test off load start
0x2205 : Test off load end
0x2206 : Test off load failed
0x2207 : External order on load start
0x2208 : External order on load end
0x2209 : External order on load failed
0x220A : External order off load start
0x220B : External order off load end
0x220C : External order off load failed
0x220D : Battery charger start
0x220E : Battery charger end
0x220F : Unlimited TOF/TOL stopped because of communication timeout
0x2301 : Automatic switch to position 0
0x2302 : Automatic switch to position 1
0x2303 : Automatic switch to position 2
0x2304 : Manual switch to position 0
0x2305 : Manual switch to position 1
0x2306 : Manual switch to position 2
0x2307 : Remote controlled switch to position 0
0x2308 : Remote controlled switch to position 1
0x2309 : Remote controlled switch to position 2
0x230A : Operating Factor Fault
0x230B : Position 0 not reached
0x230C : Position 1 not reached
0x230D : Position 2 not reached
0x230E : Unexpected switch to pos 0 when in auto mode
0x230F : Unexpected switch to pos 1 when in auto mode
0x2310 : Unexpected switch to pos 2 when in auto mode
0x2311 : Unexpected switch to pos 0 when in locked mode
0x2312 : Unexpected switch to pos 1 when in locked mode
0x2313 : Unexpected switch to pos 2 when in locked mode
0x2314 : In Phase Transfer Bypassed
0x2315 : In Phase Transfer Inhibited
0x2316 : In Phase Transfer Start
0x2317 : In Phase Transfer End
0x2318 : Breaker 1 Tripped
0x2319 : Breaker 2 Tripped
0x231A : Both Devices Tripped
0x231B : Breaker 1 Trip Reset
0x231C : Breaker 2 Trip Reset
0x231D : Commutation of BP1
0x231E : Commutation of BP2
0x231F : Breaker 1 Disconnected
0x2320 : Breaker 2 Disconnected
0x2321 : Unknown Position
0x2322 : Breaker 1 Reconnected
0x2323 : Breaker 2 Reconnected
0x2401 : Input/Output configuration changed
0x2402 : Application/Timers configuration changed
0x2403 : Sources (thresholds) configuration changed
0x2404 : Communication configuration changed
0x2405 : HMI configuration changed
0x2406 : Network configuration changed
0x2409 : Default configuration loaded
0x240F : Config Change Failed
0x2410 : Password Changed
0x2412 : Load Config Changed
0x2413 : Exerciser Config Changed
0x2414 : Timer Config Changed
0x2415 : Alarm Config Changed
0x2501 : 1FT - Primary Source fail timer start
0x251F : 1FT - Primary Source fail timer
0x2502 : 1AT/1RT - Primary Source availability/return timer start
0x2520 : 1AT/1RT - Primary Source availability/return timer stop
0x2503 : 1CT - Primary Source cooldown timer start
0x2521 : 1CT - Primary Source cooldown timer stop
0x2504 : 10T - Primary Source return to 0 timer start
0x2522 : 10T - Primary Source return to 0 timer stop
0x2505 : 1ST - Primary Source wait for start timer start
0x2523 : 1ST - Primary Source wait for start timer stop
0x2506 : 1EET - Primary Source battery charger timeout start
0x2524 : 1EET - Primary Source battery charger timeout stop
0x2507 : 1EDT - Primary Source battery charger duration start
0x2525 : 1EDT - Primary Source battery charger duration stop
0x2508 : 2FT - Secondary Source fail timer start
0x2526 : 2FT - Secondary Source fail timer stop
0x2509 : 2AT/2RT - Secondary Source availability/return timer start
0x2527 : 2AT/2RT - Secondary Source availability/return timer stop
0x250A : 2CT - Secondary Source cooldown timer start
0x2528 : 2CT - Secondary Source cooldown timer stop
0x250B : 20T - Secondary Source return to 0 timer start
0x2529 : 20T - Secondary Source return to 0 timer stop
0x250C : 2ST - Secondary Source wait for start timer start
0x252A : 2ST - Secondary Source wait for start timer stop
0x250D : 2EET - Secondary Source battery charger timeout start
0x252B : 2EET - Secondary Source battery charger timeout stop
0x250E : 2EDT - Secondary Source battery charger duration start
0x252C : 2EDT - Secondary Source battery charger duration stop
0x250F : DBT - Dead band timer start
0x252D : DBT - Dead band timer stop
0x2510 : TOL - Test on load duration timer start
0x252E : TOL - Test on load duration timer stop
0x2511 : T3T - Test on load end timer start
0x252F : T3T - Test on load end timer stop
0x2512 : TOF - Test off load duration timer start
0x2530 : TOF - Test off load duration timer stop
0x2513 : E1T - Time before external order on load start
0x2531 : E1T - Time before external order on load stop
0x2514 : E3T - Time after external order on load start
0x2532 : E3T - Time after external order on load stop
0x2515 : E2T - External order on load duration start
0x2533 : E2T - External order on load duration stop
0x2516 : E5T - Time before external order off load start
0x2534 : E5T - Time before external order off load stop
0x2517 : E7T - Time after external order off load start
0x2535 : E7T - Time after external order off load stop
0x2518 : E6T - External order off load duration start
0x2536 : E6T - External order off load duration stop
0x2519 : LSD - LoadShedding_On Timer start
0x2537 : LSD - LoadShedding_On Timer stop
0x251A : LSR - LoadShedding_Off Timer start
0x2538 : LSR - LoadShedding_Off Timer stop
0x251C : StartGen idle timer start
0x253A : StartGen idle timer stop
0x251D : 1CY - Source 1 Cycler Timer start
0x253B : 1CY - Source 1 Cycler Timer stop
0x251E : 2CY - Source 2 Cycler Timer start
0x253C : 2CY - Source 2 Cycler Timer stop
0x2601 : Switched to auto mode
0x2602 : Switched to manual mode
0x2603 : Switched to locked mode
0x2604 : Switched to control mode
0x2605 : Retransfer validated
0x2606 : Test off load validated
0x2607 : Alarms / Faults reset
0x2608 : Product becomes available
0x2609 : Product becomes unavailable
0x260A : Product becomes inhibited
0x260B : Product no more inhibited
0x260C : Start Bypass Paralelling
0x260D : Start Bypass Test
0x260E : Start Bypass Emergency
0x260F : Start Bypass Normal
0x2610 : End Bypass Paralelling
0x2611 : End Bypass Test
0x2612 : End Bypass Emergency
0x2613 : End Bypass Normal
0x2706 : Source 1 Time meter reset
0x270C : Source 2 Time meter reset
0x270D : Start order count reset
0x270E : Start order active duration reset
0x270F : Secondary source duration reset
0x2710 : Secondary source active duration reset
0x2711 : Source 1 load supplied duration reset
0x2712 : Source 2 load supplied duration reset
0x2713 : Cycle Counter Reset
0x2714 : Partial Position Timer Meter Counter Reset
0x2715 : Operating Hours Counter Reset
0x2716 : Genset 1 Stats Reset
0x2717 : Bypass Stats Reset
0x2718 : Trip 1 Stats Reset
0x2719 : Trip 2 Stats Reset
0x271A : Genset 2 Stats Reset
0x2801 : Load shedding request activated
0x2802 : Load shedding request deactivated
0x2803 : Elevator activated
0x2804 : Elevator deactivated
0x2805 : Backup GenGen Requested
0x2806 : Backup GenGen Cancelled
0x2807 : Genset Source 1 Started
0x2808 : Genset Source 1 Stopped
0x2809 : Genset Source 2 Started
0x280A : Genset Source 2 Stopped
0x2901 : Exerciser 1 Started
0x2902 : Exerciser 1 Stopped
0x2903 : Exerciser 2 Started
0x2904 : Exerciser 2 Stopped
0x2905 : Exerciser 3 Started
0x2906 : Exerciser 3 Stopped
0x2907 : Exerciser 4 Started
0x2908 : Exerciser 4 Stopped
0x4002 : Alarm Log Cleared
0x4003 : Event Log Cleared
0x4100 : Context Load Failed
0x4101 : Context Save Failed
0x4200 : Inspection Took Place
0x4201 : Passwords Reset
0x4202 : Phone Number Changed
0x4203 : Open Door
0x4204 : Product Padlocked
0x4205 : Interlock Failed
0x4206 : Maintenance Access
0x4207 : Factory Access
0x8000 : Power On
0x8001 : Power Off
0x8100 : Configuration changed
0x8101 : Configuration save failed
0x8102 : Configuration load failed
0x8105 : Configuration date saved
0x8106 : Configuration date save failed
0x8107 : Configuration date read failed
0x8110 : Configuration calibration read failed
0x8200 : Total Energy meters set
0x8201 : Partial Energy meters reset
0x8300 : User reset
0x8301 : Watchdog reset
0x8305 : Hard Reset
0x8306 : Device Reboot
| 4740 | 0x1284 | 2 | Start Date | s | DATETIME | Data | NONE | READ | READ
| 4742 | 0x1286 | 1 | Cause | - | U16_HEX | Data | NONE | READ | READ
| 4743 | 0x1287 | 1 | Status | - | U16 | Data | USER | NONE | WRITE
0 : Active
1 : Finished
| 4744 | 0x1288 | 1 | Reserved U16 | - | S16 | Data | NONE | READ | READ
| 4745 | 0x1289 | 2 | Reserved U32 | - | S32 | Data | NONE | READ | READ
Analog-Maintenance
ALM Ana Maint Current Status #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5029 | 0x13A5 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5030 | 0x13A6 | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5031 | 0x13A7 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5032 | 0x13A8 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5033 | 0x13A9 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5035 | 0x13AB | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5037 | 0x13AD | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5039 | 0x13AF | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5040 | 0x13B0 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5041 | 0x13B1 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5042 | 0x13B2 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5043 | 0x13B3 | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5044 | 0x13B4 | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5048 | 0x13B8 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
ALM Ana Maint Current Status #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5053 | 0x13BD | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5054 | 0x13BE | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5055 | 0x13BF | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5056 | 0x13C0 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5057 | 0x13C1 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5059 | 0x13C3 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5061 | 0x13C5 | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5063 | 0x13C7 | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5064 | 0x13C8 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5065 | 0x13C9 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5066 | 0x13CA | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5067 | 0x13CB | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5068 | 0x13CC | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5072 | 0x13D0 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
ALM Ana Maint Current Status #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5077 | 0x13D5 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5078 | 0x13D6 | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5079 | 0x13D7 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5080 | 0x13D8 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5081 | 0x13D9 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5083 | 0x13DB | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5085 | 0x13DD | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5087 | 0x13DF | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5088 | 0x13E0 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5089 | 0x13E1 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5090 | 0x13E2 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5091 | 0x13E3 | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5092 | 0x13E4 | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5096 | 0x13E8 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
ALM Ana Maint Current Status #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5101 | 0x13ED | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5102 | 0x13EE | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5103 | 0x13EF | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5104 | 0x13F0 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5105 | 0x13F1 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5107 | 0x13F3 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5109 | 0x13F5 | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5111 | 0x13F7 | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5112 | 0x13F8 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5113 | 0x13F9 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5114 | 0x13FA | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5115 | 0x13FB | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5116 | 0x13FC | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5120 | 0x1400 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
ALM Ana Maint Current Status #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5125 | 0x1405 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5126 | 0x1406 | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5127 | 0x1407 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5128 | 0x1408 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5129 | 0x1409 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5131 | 0x140B | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5133 | 0x140D | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5135 | 0x140F | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5136 | 0x1410 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5137 | 0x1411 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5138 | 0x1412 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5139 | 0x1413 | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5140 | 0x1414 | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5144 | 0x1418 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
ALM Ana Maint Current Status #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5149 | 0x141D | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5150 | 0x141E | 1 | Status | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5151 | 0x141F | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
19 : Maintenance
| 5152 | 0x1420 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5153 | 0x1421 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5155 | 0x1423 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5157 | 0x1425 | 2 | Analog variable (ServiceID) | - | U32 | Info | NONE | READ | READ
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time since last inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 5159 | 0x1427 | 1 | Analog variable (Instance index) | - | U16 | Info | NONE | READ | READ
| 5160 | 0x1428 | 1 | Analog variable (Instance type) | - | U16 | Info | NONE | READ | READ
| 5161 | 0x1429 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5162 | 0x142A | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 5163 | 0x142B | 1 | Hysteresis | % / 10 | U16 | Info | NONE | READ | READ
| 5164 | 0x142C | 4 | Threshold | - | S64 | Info | NONE | READ | READ
| 5168 | 0x1430 | 4 | Min/Max | - | S64 | Info | NONE | READ | READ
Logical
ALM Log Current Status #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5456 | 0x1550 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5457 | 0x1551 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5458 | 0x1552 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
7 : Logical Active
| 5459 | 0x1553 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5460 | 0x1554 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5462 | 0x1556 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5464 | 0x1558 | 1 | Logical input | - | U8 | Info | NONE | READ | READ
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5465 | 0x1559 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5466 | 0x155A | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
ALM Log Current Status #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5467 | 0x155B | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5468 | 0x155C | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5469 | 0x155D | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
7 : Logical Active
| 5470 | 0x155E | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5471 | 0x155F | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5473 | 0x1561 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5475 | 0x1563 | 1 | Logical input | - | U8 | Info | NONE | READ | READ
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5476 | 0x1564 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5477 | 0x1565 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
ALM Log Current Status #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5478 | 0x1566 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5479 | 0x1567 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5480 | 0x1568 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
7 : Logical Active
| 5481 | 0x1569 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5482 | 0x156A | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5484 | 0x156C | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5486 | 0x156E | 1 | Logical input | - | U8 | Info | NONE | READ | READ
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5487 | 0x156F | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5488 | 0x1570 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
ALM Log Current Status #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5489 | 0x1571 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5490 | 0x1572 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5491 | 0x1573 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
7 : Logical Active
| 5492 | 0x1574 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5493 | 0x1575 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5495 | 0x1577 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 5497 | 0x1579 | 1 | Logical input | - | U8 | Info | NONE | READ | READ
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5498 | 0x157A | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 5499 | 0x157B | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
System
ALM Sys Current Status #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6400 | 0x1900 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6401 | 0x1901 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6402 | 0x1902 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6403 | 0x1903 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6404 | 0x1904 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6405 | 0x1905 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6407 | 0x1907 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6409 | 0x1909 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6410 | 0x190A | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6411 | 0x190B | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6413 | 0x190D | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6414 | 0x190E | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6415 | 0x190F | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6419 | 0x1913 | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6423 | 0x1917 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6424 | 0x1918 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6425 | 0x1919 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6426 | 0x191A | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6427 | 0x191B | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6428 | 0x191C | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6430 | 0x191E | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6432 | 0x1920 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6433 | 0x1921 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6434 | 0x1922 | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6436 | 0x1924 | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6437 | 0x1925 | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6438 | 0x1926 | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6442 | 0x192A | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6446 | 0x192E | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6447 | 0x192F | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6448 | 0x1930 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6449 | 0x1931 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6450 | 0x1932 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6451 | 0x1933 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6453 | 0x1935 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6455 | 0x1937 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6456 | 0x1938 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6457 | 0x1939 | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6459 | 0x193B | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6460 | 0x193C | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6461 | 0x193D | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6465 | 0x1941 | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6469 | 0x1945 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6470 | 0x1946 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6471 | 0x1947 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6472 | 0x1948 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6473 | 0x1949 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6474 | 0x194A | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6476 | 0x194C | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6478 | 0x194E | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6479 | 0x194F | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6480 | 0x1950 | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6482 | 0x1952 | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6483 | 0x1953 | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6484 | 0x1954 | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6488 | 0x1958 | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6492 | 0x195C | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6493 | 0x195D | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6494 | 0x195E | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6495 | 0x195F | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6496 | 0x1960 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6497 | 0x1961 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6499 | 0x1963 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6501 | 0x1965 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6502 | 0x1966 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6503 | 0x1967 | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6505 | 0x1969 | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6506 | 0x196A | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6507 | 0x196B | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6511 | 0x196F | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6515 | 0x1973 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6516 | 0x1974 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6517 | 0x1975 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6518 | 0x1976 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6519 | 0x1977 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6520 | 0x1978 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6522 | 0x197A | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6524 | 0x197C | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6525 | 0x197D | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6526 | 0x197E | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6528 | 0x1980 | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6529 | 0x1981 | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6530 | 0x1982 | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6534 | 0x1986 | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
ALM Sys Current Status #7
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6538 | 0x198A | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6539 | 0x198B | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6540 | 0x198C | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Net Rotation
20 : External Alarm
21 : I/O Connection Failure
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6541 | 0x198D | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
12 : System Active
| 6542 | 0x198E | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6543 | 0x198F | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6545 | 0x1991 | 2 | Duration | s | U32 | Info | NONE | READ | READ
| 6547 | 0x1993 | 1 | Startup delay | s / 2 | U16 | Info | NONE | READ | READ
| 6548 | 0x1994 | 1 | Dropout delay | s / 2 | U16 | Info | NONE | READ | READ
| 6549 | 0x1995 | 2 | SpeData 1 | - | U32 | Info | NONE | READ | READ
| 6551 | 0x1997 | 1 | SpeData 5 | - | U16 | Info | NONE | READ | READ
| 6552 | 0x1998 | 1 | SpeData 6 | - | U16 | Info | NONE | READ | READ
| 6553 | 0x1999 | 4 | SpeData 7 | - | S64 | Info | NONE | READ | READ
| 6557 | 0x199D | 4 | SpeData 8 | - | S64 | Info | NONE | READ | READ
Faults
ALM Fault Current Status #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5952 | 0x1740 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5953 | 0x1741 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5954 | 0x1742 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 5955 | 0x1743 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 5956 | 0x1744 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5957 | 0x1745 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5959 | 0x1747 | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5975 | 0x1757 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5976 | 0x1758 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 5977 | 0x1759 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 5978 | 0x175A | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 5979 | 0x175B | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 5980 | 0x175C | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 5982 | 0x175E | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5998 | 0x176E | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 5999 | 0x176F | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6000 | 0x1770 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 6001 | 0x1771 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 6002 | 0x1772 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6003 | 0x1773 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6005 | 0x1775 | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6021 | 0x1785 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6022 | 0x1786 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6023 | 0x1787 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 6024 | 0x1788 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 6025 | 0x1789 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6026 | 0x178A | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6028 | 0x178C | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6044 | 0x179C | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6045 | 0x179D | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6046 | 0x179E | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 6047 | 0x179F | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 6048 | 0x17A0 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6049 | 0x17A1 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6051 | 0x17A3 | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6067 | 0x17B3 | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6068 | 0x17B4 | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6069 | 0x17B5 | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 6070 | 0x17B6 | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 6071 | 0x17B7 | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6072 | 0x17B8 | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6074 | 0x17BA | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALM Fault Current Status #7
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6090 | 0x17CA | 1 | Ack ID | - | U16 | Info | NONE | READ | READ
| 6091 | 0x17CB | 1 | Status : | - | U8 | Info | NONE | READ | READ
0 : Inactive
1 : Active
2 : Finished
3 : FinishedAndAck
| 6092 | 0x17CC | 1 | Alarm Type | - | U8 | Info | NONE | READ | READ
0 : None
1 : Unexpected Transfer
2 : Failed to Transfer
3 : Operating Factor Fault
4 : Max PWD Attempts
5 : Genset Failed to Start
6 : External Fault
7 : Unknown Position
| 6093 | 0x17CD | 1 | Alarm cause : | - | U8 | Info | NONE | READ | READ
0 : Cause Unknown
20 : Fault Active
| 6094 | 0x17CE | 1 | Criticality : | - | U8 | Info | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 6095 | 0x17CF | 2 | Start date | - | DATETIME | Info | NONE | READ | READ
| 6097 | 0x17D1 | 2 | Duration | s | U32 | Info | NONE | READ | READ
ALARM Log
Command
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 9120 | 0x23A0 | 1 | Start record number (0 to 65534) or 65535 for last record | - | U16 | Command | NONE | WRITE_MANY | WRITE_MANY
Header
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 9136 | 0x23B0 | 1 | Next record number | - | U16 | Header | NONE | READ | READ
| 9137 | 0x23B1 | 1 | Items count (max 7 per request) | - | U16 | Header | NONE | READ | READ
| 9138 | 0x23B2 | 1 | Item size (words) | - | U16 | Header | NONE | READ | READ
Data
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 9139 | 0x23B3 | 1 | Alarm cause | - | U16_HEX | Data | NONE | READ | READ
0 : Cause Unknown
1 : Analog. High Th. Single
2 : Analog. High Th. Tri. And
3 : Analog. High Th. Tri. Or
4 : Analog. Low Th Single
5 : Analog. Low Th. Tri. And
6 : Analog. Low Th. Tri. Or
7 : Logical Active
8 : Combi. And
9 : Combi. Or
10 : EN50160 Active
11 : Inrush Active
12 : System Active
19 : Maintenance
20 : Fault
| 9140 | 0x23B4 | 1 | Criticality : | - | U8 | Data | NONE | READ | READ
0 : Information
1 : Warning
2 : Critical
| 9141 | 0x23B5 | 2 | Start date | - | DATETIME | Data | NONE | READ | READ
| 9143 | 0x23B7 | 2 | Duration | s | U32 | Data | NONE | READ | READ
| 9145 | 0x23B9 | 2 | Specific data 1 (depend on alarm type) | - | U32 | Data | NONE | READ | READ
| 9147 | 0x23BB | 1 | Specific data 2 (depend on alarm type) | - | U16 | Data | NONE | READ | READ
| 9148 | 0x23BC | 1 | Specific data 3 (depend on alarm type) | - | U16 | Data | NONE | READ | READ
| 9149 | 0x23BD | 1 | Specific data 4 (depend on alarm type) | - | U16 | Data | NONE | READ | READ
| 9150 | 0x23BE | 1 | Specific data 5 (depend on alarm type) | - | U16 | Data | NONE | READ | READ
| 9151 | 0x23BF | 1 | Specific data 6 (depend on alarm type) | - | U16 | Data | NONE | READ | READ
| 9152 | 0x23C0 | 4 | Specific data 7 (depend on alarm type) | - | S64 | Data | NONE | READ | READ
| 9156 | 0x23C4 | 4 | Specific data 8 (depend on alarm type) | - | S64 | Data | NONE | READ | READ
Settings
Setup Network
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 12288 | 0x3000 | 1 | Network connection type | - | U8 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
0 : Not defined
1 : 1P + N
2 : 2P
3 : 2P + N
4 : 3P
5 : 3P + N
7 : 3P + N / 1P + N
| 12289 | 0x3001 | 2 | Nominal Voltage | V | U32 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
| 12291 | 0x3003 | 1 | Nominal Frequency | - | U8 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
0 : 50 Hz - eDefFnom_50Hz
1 : 60 Hz - eDefFnom_60Hz
| 12292 | 0x3004 | 1 | Phase Rotation | - | U8 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
0 : V1 - V2 - V3
1 : V1 - V3 - V2
| 12293 | 0x3005 | 1 | Voltage transformer used | - | U8 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 12294 | 0x3006 | 2 | Voltage transformer rate : primary | - | U32 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
| 12296 | 0x3008 | 1 | Voltage transformer rate : secondary | - | U16 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
| 12297 | 0x3009 | 1 | Phase Rotation Check | - | U8 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
Network Autodetection
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 12368 | 0x3050 | 1 | Autodetect network | - | U8 | Commands | USER | NONE | WRITE
0 : No action
1 : Start Autodetection
Setup Threshold for up stream Voltages
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 22272 | 0x5700 | 1 | Source 1 : Overvoltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22273 | 0x5701 | 1 | Source 1 : Overvoltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22274 | 0x5702 | 1 | Source 1 : Undervoltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22275 | 0x5703 | 1 | Source 1 : Undervoltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22276 | 0x5704 | 1 | Source 2 : Overvoltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22277 | 0x5705 | 1 | Source 2 : Overvoltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22278 | 0x5706 | 1 | Source 2 : Undervoltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22279 | 0x5707 | 1 | Source 2 : Undervoltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22280 | 0x5708 | 1 | Source 1 : Unbalanced voltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22281 | 0x5709 | 1 | Source 1 : Unbalanced voltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22282 | 0x570A | 1 | Source 2 : Unbalanced voltage threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22283 | 0x570B | 1 | Source 2 : Unbalanced voltage hysteresis threshold | % | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22284 | 0x570C | 1 | Source 1 : Overfrequency threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22285 | 0x570D | 1 | Source 1 : Overfrequency hysteresis threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22286 | 0x570E | 1 | Source 1 : Underfrequency threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22287 | 0x570F | 1 | Source 1 : Underfrequency hysteresis threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22288 | 0x5710 | 1 | Source 2 : Overfrequency threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22289 | 0x5711 | 1 | Source 2 : Overfrequency hysteresis threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22290 | 0x5712 | 1 | Source 2 : Underfrequency threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22291 | 0x5713 | 1 | Source 2 : Underfrequency hysteresis threshold | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ATS Aplication
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 22064 | 0x5630 | 1 | Type of Application | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : M-M
1 : M-G
2 : G-G
| 22065 | 0x5631 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22066 | 0x5632 | 1 | External position command logic type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : CONTACT
1 : IMPULSE
| 22067 | 0x5633 | 1 | Priority - Power Supply | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Network
1 : Source 1
2 : Source 2
| 22068 | 0x5634 | 1 | Priority - Test On Load | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 22069 | 0x5635 | 1 | Priority - External Order On Load | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 22070 | 0x5636 | 1 | Manual retransfer | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 22071 | 0x5637 | 1 | Return to Zero function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 22072 | 0x5638 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22073 | 0x5639 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22074 | 0x563A | 1 | Switch Technology | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
1 : HIB4xxM
2 : Contactor
3 : Circuit Breaker
| 22075 | 0x563B | 1 | Test Button use | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Test Off Load
1 : Test On Load
| 22076 | 0x563C | 1 | Op. Factor : Nb of operations | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22077 | 0x563D | 1 | Op. Factor : Time for nb of operations | min | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22078 | 0x563E | 16 | Source1 Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22094 | 0x564E | 16 | Source2 Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22110 | 0x565E | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22111 | 0x565F | 1 | Retry number | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22112 | 0x5660 | 1 | Retry delay | s 10⁻³ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22113 | 0x5661 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22114 | 0x5662 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22115 | 0x5663 | 1 | Power Up In Auto | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : YES
| 22116 | 0x5664 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22117 | 0x5665 | 1 | Load adding delays | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : To Source 2 only
2 : To Source 1 only
3 : Always Enabled
Timers
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 22016 | 0x5600 | 1 | 1FT Source1 Failure Timer | s 10⁻¹ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22017 | 0x5601 | 1 | 1RT Source1 Available/Return Timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22018 | 0x5602 | 1 | 1CT Source1 Genset Cooldown timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22019 | 0x5603 | 1 | 10T Source1 return to 0 timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22020 | 0x5604 | 1 | 1ST Source1 Start TimeOut timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22021 | 0x5605 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22022 | 0x5606 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22023 | 0x5607 | 1 | 2FT Source2 Failure Timer | s 10⁻¹ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22024 | 0x5608 | 1 | 2RT Source2 Available/Return Timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22025 | 0x5609 | 1 | 2CT Source2 Genset Cooldown timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22026 | 0x560A | 1 | 20T Source2 return to 0 timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22027 | 0x560B | 1 | 2ST Source2 Start TimeOut timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22028 | 0x560C | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22029 | 0x560D | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22030 | 0x560E | 1 | DBT Dead Band timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22031 | 0x560F | 1 | Limit_TOT Test on load is limited | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : unlimited
1 : limited
| 22032 | 0x5610 | 1 | TOT Test on load duration timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22033 | 0x5611 | 1 | T3T Test on load end timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22034 | 0x5612 | 1 | Limit_TFT Test off load is limited | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : unlimited
1 : limited
| 22035 | 0x5613 | 1 | TFT Test off load duration timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22036 | 0x5614 | 1 | E1T Time before external order on load | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22037 | 0x5615 | 1 | E3T Time after external order on load | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22038 | 0x5616 | 1 | Limit_E2T External order on load is limited | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : unlimited
1 : limited
| 22039 | 0x5617 | 1 | E2T External order on load duration | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22040 | 0x5618 | 1 | E5T Time before external order off load | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22041 | 0x5619 | 1 | E7T Time after external order off load | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22042 | 0x561A | 1 | Limit_E6T External order off load is limited | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : unlimited
1 : limited
| 22043 | 0x561B | 1 | E6T External order off load duration | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22044 | 0x561C | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22045 | 0x561D | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22046 | 0x561E | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22047 | 0x561F | 1 | DRT: Dynamic return timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22048 | 0x5620 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22049 | 0x5621 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22050 | 0x5622 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22051 | 0x5623 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22052 | 0x5624 | 1 | OD1: On Delay 1 Timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22053 | 0x5625 | 1 | OD2: On Delay 2 Timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22054 | 0x5626 | 1 | OD3: On Delay 3 Timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22055 | 0x5627 | 1 | CH1: Charging Time Duration Breaker 1 | s 10⁻¹ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22056 | 0x5628 | 1 | CH2: Charging Time Duration Breaker 2 | s 10⁻¹ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22057 | 0x5629 | 1 | 1CY: Source 1 Cycler Duration | h | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22058 | 0x562A | 1 | 2CY: Source 2 Cycler Duration | h | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 22059 | 0x562B | 1 | PreODx : On Delay pre-transfer timer | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Exerciser
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 24064 | 0x5E00 | 1 | Custom1: Exerciser Type set | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Not Used
1 : For TON
2 : For TOF
| 24065 | 0x5E01 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24066 | 0x5E02 | 1 | Custom1: Periodic Schedule Set | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Daily
1 : Weekly
2 : Bi Weekly
3 : Monthly
4 : Yearly
5 : Non Cyclic
6 : Bi Daily
7 : Bi Monthly
8 : Hexa Monthly
9 : 28 Days
| 24067 | 0x5E03 | 2 | Custom1 Start Time | - | DATETIME | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24069 | 0x5E05 | 1 | Custom1 Duration | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24070 | 0x5E06 | 2 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24072 | 0x5E08 | 1 | Min Idle Time to Run | min | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Cycler_Breaker
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 24144 | 0x5E50 | 1 | Cycler Status | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 24145 | 0x5E51 | 1 | Transfer strategy between cycles | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Automatic
1 : Specifc time
| 24146 | 0x5E52 | 1 | Transfer time : Hour | h | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24147 | 0x5E53 | 1 | Transfer time : Minute | min | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 24148 | 0x5E54 | 1 | Backup Gen Gen start mode (prio selection) | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Least used
1 : Alternate
2 : Priority source
3 : Full cycles
| 24149 | 0x5E55 | 1 | Tripping Action of Breaker 1 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Partial Inhibit
1 : Inhibit
2 : Total Inhibit
3 : Trip = Source Lost
| 24150 | 0x5E56 | 1 | Operating Mode after trip for Breaker 1 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Inhibit
1 : Previous Mode
2 : Auto
3 : Partial Inhibit
| 24151 | 0x5E57 | 1 | Charging time Status for Breaker 1 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : When Opened
2 : When Closed
| 24152 | 0x5E58 | 1 | Tripping Action of Breaker 2 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Partial Inhibit
1 : Inhibit
2 : Total Inhibit
3 : Trip = Source Lost
| 24153 | 0x5E59 | 1 | Operating Mode after trip for Breaker 2 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Inhibit
1 : Previous Mode
2 : Auto
3 : Partial Inhibit
| 24154 | 0x5E5A | 1 | Charging time Status for Breaker 2 | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : When Opened
2 : When Closed
Output Relay
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 16384 | 0x4000 | 1 | Output 1 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16385 | 0x4001 | 1 | Output 2 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16386 | 0x4002 | 1 | Output 3 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16387 | 0x4003 | 1 | Output 4 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
70 : PO1 - Position 1 order / Close Breaker 1
71 : PO2 - Position 2 order / Close Breaker 2
72 : PO0 - Position 0 order
73 : PA0 - Position 0 order Source 1 / Open Breaker 1
74 : PB0 - Position 0 order Source 2 / Open Breaker 2
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16388 | 0x4004 | 1 | Output 1 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 16389 | 0x4005 | 1 | Output 2 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 16390 | 0x4006 | 1 | Output 3 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 16391 | 0x4007 | 1 | Output 4 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 16392 | 0x4008 | 1 | Pulse length (RTSE control in pulse mode) | s 10⁻³ | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 16393 | 0x4009 | 1 | Output 5 function (Genset S1) | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
75 : GS1 - Genset Source 1 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16394 | 0x400A | 1 | Output 6 function (Genset S2) | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
75 : GS1 - Genset Source 1 start
76 : GS2 - Genset Source 2 start
77 : S1A - Source 1 available
78 : S2A - Source 2 available
79 : SCA - At Least 1 source avail
80 : S1U - Source 1 unavailable
81 : S2U - Source 2 unavailable
82 : AC1 - Source 1 closed
83 : AC2 - Source 2 closed
84 : AC0 - Off Position
88 : FLT - Faults active
94 : ROS - TON or EON in progress
109 : AUD - Critical Alarm Active
133 : OD1 - On Delay 1 output
134 : OD2 - On Delay 2 output
135 : OD3 - On Delay 3 output
| 16395 | 0x400B | 1 | Output 5 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 16396 | 0x400C | 1 | Output 6 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
Input
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 11296 | 0x2C20 | 1 | Input 1 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11297 | 0x2C21 | 1 | Input 2 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11298 | 0x2C22 | 1 | Input 3 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11299 | 0x2C23 | 1 | Input 4 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11300 | 0x2C24 | 1 | Input 5 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11301 | 0x2C25 | 1 | Input 6 function | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : --- - None
21 : INH - Inhibition
22 : INHP - Partial Inhibition
23 : INHT - Total Inhibition
24 : TON - Test on load
25 : TOF - Test off load
26 : EON - External order on load
27 : EOF - External order off load
28 : MRT - Manual Retransfer
29 : PRI - Change Priority
30 : SS1 - Validation Stabilization source 1
31 : SS2 - Validation Stabilization source 2
32 : ALE - External Alarm
33 : FTE - External Fault
34 : DIS1 - Breaker 1 disconnected
35 : DIS2 - Breaker 2 disconnected
36 : MSR - Priority test on load
37 : OA1 - Override source 1 available
38 : OA2 - Override source 2 available
39 : OU1 - Override source 1 unavailable
40 : OU2 - Override source 2 unavailable
41 : RST - Reset faults state
43 : AC1 - Switch in position 1 / Breaker 1 closed
44 : AC2 - Switch in position 2 / Breaker 2 closed
45 : AC0 - Switch in position 0
46 : AC0A - Switch Source 1 in position 0 / Breaker 1 open
47 : AC0B - Switch Source 2 in position 0 / Breaker 2 open
48 : MAN - RTSE in manual mode
49 : LCK - RTSE locked
50 : CHP - Change Position
53 : PS1 - Go to position 1
54 : PS2 - Go to position 2
55 : PS0 - Go to position 0
56 : RT0 - Return to 0 position
57 : BLK - Interlocking blocked
58 : TP1 - Trip Breaker 1
59 : TP2 - Trip Breaker 2
60 : REC - Remote control
61 : EST - Emergency Signal
64 : BCT - Bypass Current Timer
68 : CYC - Cycler Enable
69 : EGG - Enable Gen/Gen backup
125 : CH1 - Breaker 1 Charged
126 : CH2 - Breaker 2 Charged
| 11302 | 0x2C26 | 1 | Input 1 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 11303 | 0x2C27 | 1 | Input 2 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 11304 | 0x2C28 | 1 | Input 3 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 11305 | 0x2C29 | 1 | Input 4 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 11306 | 0x2C2A | 1 | Input 5 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
| 11307 | 0x2C2B | 1 | Input 6 type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : NO
1 : NC
Communication - Slave address
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57344 | 0xE000 | 1 | Slave Address | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Communication - Modbus slave connection settings RS485
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57345 | 0xE001 | 1 | Baudrate : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : 1200
1 : 2400
2 : 4800
3 : 9600
4 : 19200
5 : 38400
6 : 57600
7 : 115200
| 57346 | 0xE002 | 1 | Stop bit : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : 1
1 : 2
| 57347 | 0xE003 | 1 | Parity : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Odd
2 : Even
Communication - Hour/Date
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57600 | 0xE100 | 1 | Day | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 57601 | 0xE101 | 1 | Month | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 57602 | 0xE102 | 1 | Year | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 57603 | 0xE103 | 1 | Hour | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 57604 | 0xE104 | 1 | Minute | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 57605 | 0xE105 | 1 | Second | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Communication - Screen interface settings
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 28928 | 0x7100 | 1 | Language | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : English
1 : French
2 : German
3 : Italian
4 : Polish
5 : Spanish
6 : Turkish
8 : Chinese
9 : Portuguese
| 28929 | 0x7101 | 1 | Backlight intensity | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 28930 | 0x7102 | 1 | Backlight timeout | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 28931 | 0x7103 | 1 | Contrast | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Dark
1 : Medium
2 : Light
| 28932 | 0x7104 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 28933 | 0x7105 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 28934 | 0x7106 | 1 | LampTest Duration | s | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 28935 | 0x7107 | 1 | Popup Displayed | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Display All
1 : Hide Alarm
2 : Hide Timer
3 : Hide Alarm & Timer
Communication - SplashScreenText
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 29184 | 0x7200 | 1 | Text Police | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Arial 12 Light
1 : Arial 12
2 : Arial 16
3 : Arial 16 Bold
4 : Arial 40
| 29185 | 0x7201 | 16 | Line 1 Text | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 29201 | 0x7211 | 16 | Line 2 Text | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 29217 | 0x7221 | 16 | Line 3 Text | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 29233 | 0x7231 | 16 | Line 4 Text (not available for 40 police) | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Alarms
ALM Ana Maint Settings #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4368 | 0x1110 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4369 | 0x1111 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4370 | 0x1112 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4371 | 0x1113 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4372 | 0x1114 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4373 | 0x1115 | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4375 | 0x1117 | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4376 | 0x1118 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4377 | 0x1119 | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4378 | 0x111A | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4380 | 0x111C | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4382 | 0x111E | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4383 | 0x111F | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4384 | 0x1120 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4385 | 0x1121 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Ana Maint Settings #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4401 | 0x1131 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4402 | 0x1132 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4403 | 0x1133 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4404 | 0x1134 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4405 | 0x1135 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4406 | 0x1136 | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4408 | 0x1138 | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4409 | 0x1139 | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4410 | 0x113A | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4411 | 0x113B | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4413 | 0x113D | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4415 | 0x113F | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4416 | 0x1140 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4417 | 0x1141 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4418 | 0x1142 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Ana Maint Settings #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4434 | 0x1152 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4435 | 0x1153 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4436 | 0x1154 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4437 | 0x1155 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4438 | 0x1156 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4439 | 0x1157 | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4441 | 0x1159 | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4442 | 0x115A | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4443 | 0x115B | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4444 | 0x115C | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4446 | 0x115E | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4448 | 0x1160 | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4449 | 0x1161 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4450 | 0x1162 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4451 | 0x1163 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Ana Maint Settings #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4467 | 0x1173 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4468 | 0x1174 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4469 | 0x1175 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4470 | 0x1176 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4471 | 0x1177 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4472 | 0x1178 | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4474 | 0x117A | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4475 | 0x117B | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4476 | 0x117C | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4477 | 0x117D | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4479 | 0x117F | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4481 | 0x1181 | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4482 | 0x1182 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4483 | 0x1183 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4484 | 0x1184 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Ana Maint Settings #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4500 | 0x1194 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4501 | 0x1195 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4502 | 0x1196 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4503 | 0x1197 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4504 | 0x1198 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4505 | 0x1199 | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4507 | 0x119B | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4508 | 0x119C | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4509 | 0x119D | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4510 | 0x119E | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4512 | 0x11A0 | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4514 | 0x11A2 | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4515 | 0x11A3 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4516 | 0x11A4 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4517 | 0x11A5 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Ana Maint Settings #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 4533 | 0x11B5 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 4534 | 0x11B6 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 4535 | 0x11B7 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 4536 | 0x11B8 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 4537 | 0x11B9 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 4538 | 0x11BA | 2 | Analog variable (ServiceID) | - | U32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
5206 : Total Cycle Counter
5415 : Total Switch Counter
5434 : Genset S1 Activation Time
5435 : Genset S2 Activation Time
5436 : Genset S1 On Load Time
5437 : Genset S2 On Load Time
156094 : Time Since Last Inspection
156142 : Number of Trip breaker 1
156143 : Number of Trip breaker 2
| 4540 | 0x11BC | 1 | Analog variable (Instance index) | - | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4541 | 0x11BD | 1 | Reserved | - | - | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4542 | 0x11BE | 1 | Variable data access : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Single
1 : Triple (logical AND)
2 : Triple (logical OR)
3 : Maintenance
| 4543 | 0x11BF | 2 | High threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4545 | 0x11C1 | 2 | Low threshold | - | S32 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4547 | 0x11C3 | 1 | Hysteresis | % / 10 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4548 | 0x11C4 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4549 | 0x11C5 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 4550 | 0x11C6 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Log Settings #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5632 | 0x1600 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 5633 | 0x1601 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 5634 | 0x1602 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 5635 | 0x1603 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5636 | 0x1604 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 5637 | 0x1605 | 1 | Logical input | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5638 | 0x1606 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5639 | 0x1607 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5640 | 0x1608 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Log Settings #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5656 | 0x1618 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 5657 | 0x1619 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 5658 | 0x161A | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 5659 | 0x161B | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5660 | 0x161C | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 5661 | 0x161D | 1 | Logical input | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5662 | 0x161E | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5663 | 0x161F | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5664 | 0x1620 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Log Settings #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5680 | 0x1630 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 5681 | 0x1631 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 5682 | 0x1632 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 5683 | 0x1633 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5684 | 0x1634 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 5685 | 0x1635 | 1 | Logical input | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5686 | 0x1636 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5687 | 0x1637 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5688 | 0x1638 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Log Settings #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 5704 | 0x1648 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 5705 | 0x1649 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 5706 | 0x164A | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 5707 | 0x164B | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5708 | 0x164C | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 5709 | 0x164D | 1 | Logical input | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 5710 | 0x164E | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5711 | 0x164F | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 5712 | 0x1650 | 16 | Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #1
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6656 | 0x1A00 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6657 | 0x1A01 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6658 | 0x1A02 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6659 | 0x1A03 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6660 | 0x1A04 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6661 | 0x1A05 | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6662 | 0x1A06 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6663 | 0x1A07 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #2
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6664 | 0x1A08 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6665 | 0x1A09 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6666 | 0x1A0A | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6667 | 0x1A0B | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6668 | 0x1A0C | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6669 | 0x1A0D | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6670 | 0x1A0E | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6671 | 0x1A0F | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #3
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6672 | 0x1A10 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6673 | 0x1A11 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6674 | 0x1A12 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6675 | 0x1A13 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6676 | 0x1A14 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6677 | 0x1A15 | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6678 | 0x1A16 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6679 | 0x1A17 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #4
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6680 | 0x1A18 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6681 | 0x1A19 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6682 | 0x1A1A | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6683 | 0x1A1B | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6684 | 0x1A1C | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6685 | 0x1A1D | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6686 | 0x1A1E | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6687 | 0x1A1F | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #5
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6688 | 0x1A20 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6689 | 0x1A21 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6690 | 0x1A22 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6691 | 0x1A23 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6692 | 0x1A24 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6693 | 0x1A25 | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6694 | 0x1A26 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6695 | 0x1A27 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #6
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6696 | 0x1A28 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6697 | 0x1A29 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6698 | 0x1A2A | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6699 | 0x1A2B | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6700 | 0x1A2C | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6701 | 0x1A2D | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6702 | 0x1A2E | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6703 | 0x1A2F | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
ALM Sys Settings #7
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6704 | 0x1A30 | 1 | Status : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Disabled
1 : Enabled
| 6705 | 0x1A31 | 1 | Criticality : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Information
1 : Warning
2 : Critical
| 6706 | 0x1A32 | 1 | Acknowledgement method : | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : MODBUS only
2 : Logical input
| 6707 | 0x1A33 | 1 | Input for ack | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Input 1
1 : Input 2
2 : Input 3
3 : Input 4
4 : Input 5
5 : Input 6
255 : Not used
| 6708 | 0x1A34 | 1 | Output for report | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : Output 1
1 : Output 2
2 : Output 3
3 : Output 4
4 : Output 5
5 : Output 6
255 : Not used
| 6709 | 0x1A35 | 1 | Alarm Type | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
0 : None
1 : Net Rotation
20 : External Alarm
22 : Controller Unavailable
23 : Load Not Supplied
9 : RTC Low Battery
24 : DC Aux. Supply Out Of Bounds
27 : Genset Unexpectedly running
| 6710 | 0x1A36 | 1 | Startup delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 6711 | 0x1A37 | 1 | Dropout delay | s / 2 | U16 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Maintenance informations
Maintenance_Table
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 7680 | 0x1E00 | 16 | Product Name | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 7696 | 0x1E10 | 16 | Maintenance Phone Number | - | STRING_NORM | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 7712 | 0x1E20 | 2 | Last Inspection Date | - | DATETIME | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 7714 | 0x1E22 | 1 | Max Number of Password Attempts | - | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
| 7715 | 0x1E23 | 1 | Timeout after wrong password | min | U8 | Settings | USER | READ | READ ¦ WRITE ¦ WRITE_MANY
Commands
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 21760 | 0x5500 | 1 | Set Command / Alarm | - | U8_HEX | Commands | USER | NONE | WRITE
0x01 : Set Manual Retransfer (By Keyboard )
0x02 : Clear TOF( By Keyboard )
0x03 : Set TOF ( By Keyboard )
0x04 : Set TON ( By Keyboard )
0x05 : Set EOF ( By input )
0x06 : Set EON ( By input )
0x07 : Clear EOF ( By input )
0x08 : Clear EON ( By input )
0x0A : Clear TON ( By Keyboard )
0x10 : Clear Faults ( By input )
0x15 : Set EST Reset (By keyboard)
| 21761 | 0x5501 | 1 | Set Operating Mode | - | U16_HEX | Commands | USER | NONE | WRITE
0x0010 : Auto Mode
0x0020 : Manu Mode
0x0040 : Inhibit Mode
0x0080 : Partial Inhibit Mode
| 21762 | 0x5502 | 1 | Set Priority | - | U8 | Commands | USER | NONE | WRITE
0 : Network
1 : Source 1
2 : Source 2
| 21763 | 0x5503 | 1 | Set Position | - | U8 | Commands | USER | NONE | WRITE
1 : Position in Zero
2 : Position in 1
3 : Position in 2
| 21764 | 0x5504 | 1 | Set Genset Start Order | - | U8 | Commands | USER | NONE | WRITE
0 : GS1 start
1 : GS1 stop
2 : GS2 start
3 : GS2 stop
ALM Acknowledgment
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 6912 | 0x1B00 | 1 | Ack ID | - | U16 | Commands | NONE | WRITE | WRITE
Action system ( Write Function only )
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57856 | 0xE200 | 1 | Action : | - | U8_HEX | Commands | NONE | WRITE | WRITE
0xE5 : Restore factory settings
0xA1 : Product Configuration storage
0xB2 : Product reset
Lock system
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 58112 | 0xE300 | 1 | Code to submit | - | U16 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
| 58113 | 0xE301 | 1 | Delocker ID | - | U16 | Settings | NONE | READ ¦ WRITE ¦ WRITE_MANY | READ ¦ WRITE ¦ WRITE_MANY
USB function ( Write Function only )
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 57872 | 0xE210 | 1 | USB function : | - | U8_HEX | Commands | NONE | WRITE | WRITE
0x01 : DFU
0x02 : PCL
Maintenance
Partial operating hours counter reset
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 528 | 0x0210 | 1 | Reset command | - | U16 | Commands | USER | NONE | WRITE
0 : Reset
Reset counter and time meters
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 23376 | 0x5B50 | 1 | Reset switch counters | - | U8 | Commands | USER | NONE | WRITE
0 : No action
1 : Reset
| 23377 | 0x5B51 | 1 | Reset partial time on position counters | - | U8 | Commands | USER | NONE | WRITE
0 : No action
1 : Reset
| 23378 | 0x5B52 | 1 | Reset Genset counters | - | U8 | Commands | USER | NONE | WRITE
0 : No action
1 : Genset 1
2 : Genset 2
| 23379 | 0x5B53 | 1 | Reserved | - | - | Commands | USER | NONE | WRITE
| 23380 | 0x5B54 | 1 | Reset Breakers Trip counters | - | U8 | Commands | USER | NONE | WRITE
0 : No action
1 : Breaker 1
2 : Breaker 2
Reset histo
| Dec address | Hex address | Words count | Description | Unit | Data type | Type | Lock level | Locked fcts | Unlocked fcts
| 544 | 0x0220 | 1 | Action | - | U16 | Commands | USER | NONE | WRITE
0 : No action
1 : Reset alarms history
4 : Reset events history