## Generalities
GENERALITIES
Generalities
The JBUS/MODBUS used by the product involves a dialogue using a master-slave hierarchical structure.
There are two possible dialogues :
- The master communicates with a slave and waits for its reply
- The master communicates with all the slaves without waiting for the reply
Hager products implement functions :
- 3 : to read n Words ( Maximum 125 words )
- 6 : to write 1 word
- 16 : to write n Word
The register type used are :
|  | long | 2 Words ( 4 bytes )
|  | int | 1 Word ( 2 Words )
If the register value is not available, according to its type and its signed, the indicated value is :
|  | unsigned long |  | FFFF FFFFhex
|  | signed long |  | 7FFF FFFF hex
|  | unsigned Int |  | FFFF hex
|  | signed int |  | 7FFF hex
Function 3 : Read n Words
Function 3 : Request frame format
Function 3 : Answer frame format
Number of Word asked in the Request frame
Data format is High and low order
Function 6 :Write 1 Word
Function 6 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network ( No answer is sent by the device )
Function 6 : Answer frame format
Function 16 :Write n Words
Function 16 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network : No answer is sent by the device
Function 16 : Answer frame format
1 Byte
0 < Value < 247

## Product Tables
Product name : EC700
C650 Hex : Energies
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
Not applicable | 50768 | C650 | 2 | Hour meter | 1/100 h | 3 | 0xFFFFFFFF
Not applicable | 50770 | C652 | 2 | Total Positive Active Energy (no resetable) : Ea+ | kWh | 3 | 0xFFFFFFFF
Not applicable | 50772 | C654 | 2 | Total Positive Reactive Energy (no resetable) : Er + | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50774 | C656 | 2 | Total Apparent Energy (no resetable) : Es | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50776 | C658 | 2 | Total Negative Active Energy (no resetable) : Ea- | kWh | 3 | 0xFFFFFFFF
Not applicable | 50778 | C65A | 2 | Total Negative Reactive Energy (no resetable) : Er - | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50780 | C65C | 2 | Partial Positive Active Energy: Ea+ | kWh | 3 | 0xFFFFFFFF
Not applicable | 50782 | C65E | 2 | Partial Positive Reactive Energy: Er + | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50784 | C660 | 2 | Partial Apparent Energy : Es | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50786 | C662 | 2 | Partial Negative Active Energy : Ea- | kWh | 3 | 0xFFFFFFFF
Not applicable | 50788 | C664 | 2 | Partial Negative Reactive Energy : Er - | kvarh | 3 | 0xFFFFFFFF
| 50790 | C666 | 2 | Number of pulse meter ( 10 Maxi ) | - | 3 | 0xFFFFFFFF
| 50792 | C668 | 2 | Total pulse meter Input 1 | - | 3 | 0xFFFFFFFF
| 50794 | C66A | 2 | Total pulse meter Input 2 | - | 3 | 0xFFFFFFFF
| 50796 | C66C | 2 | Total pulse meter Input 3 | - | 3 | 0xFFFFFFFF
| 50798 | C66E | 2 | Total pulse meter Input 4 | - | 3 | 0xFFFFFFFF
| 50800 | C670 | 2 | Total pulse meter Input 5 | - | 3 | 0xFFFFFFFF
| 50802 | C672 | 2 | Total pulse meter Input 6 | - | 3 | 0xFFFFFFFF
| 50804 | C674 | 2 | Total pulse meter Input 7 | - | 3 | 0xFFFFFFFF
| 50806 | C676 | 2 | Total pulse meter Input 8 | - | 3 | 0xFFFFFFFF
| 50808 | C678 | 2 | Total pulse meter Input 9 | - | 3 | 0xFFFFFFFF
| 50810 | C67A | 2 | Total pulse meter Input 10 | - | 3 | 0xFFFFFFFF
Not applicable | 50812 | C67C | 2 | Predictive Active Power | kWh | 3 | 0xFFFFFFFF
Not applicable | 50814 | C67E | 2 | Predictive Reactive Power | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50816 | C680 | 2 | Predictive Apparent Power | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50818 | C682 | 2 | Mean positive active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
Not applicable | 50820 | C684 | 2 | Mean negative active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
Not applicable | 50822 | C686 | 2 | Mean positive reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
Not applicable | 50824 | C688 | 2 | Mean negative reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
Not applicable | 50826 | C68A | 2 | Last date for Record average P/Q/S in second since 01/01/2000 | s | 3 | 0xFFFFFFFF
Not applicable | 50828 | C68C | 1 | Last average (P+) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50829 | C68D | 1 | Last average (Q+) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50830 | C68E | 1 | Last average (P-) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50831 | C68F | 1 | Last average (Q-) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50832 | C690 | 1 | Last average S | VA ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50768 | C650 | 65
CB00 Hex : Input/Output state
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 51968 | CB00 | 1 | Input count |  | 3 | 0
| 51969 | CB01 | 1 | Bit 0 : Input 1 Open or Closed Bit x : Input x Open or Closed | Bitfield | 3
| 51970 | CB02 | 1 | Output count |  | 3 | 0
| 51971 | CB03 | 1 | Bit 0 : Output 1 Open or Closed Bit x : Output x Open or Closed | Bitfield | 3
| 51968 | CB00 | 4
D000 Hex : Events Table
Element Definition
|  |  | 1 | Table Address
|  |  | 1 | 1:Table Updated / 0: Table not updated
2
Header | 53248 | D000 | 1 | Table Size |  | 3
| 53249 | D001 | 1 | Header size |  | 3
| 53250 | D002 | 1 | Element Count |  | 3
| 53251 | D003 | 2 | Element definition |  | 3
| 53253 | D005 | 2 | Element definition |  | 3
| 53248 | D000 | 2 Mini
E100 Hex :Hour/Date setting ( Write 6 words in one time Function 16)
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57600 | E100 | 1 | Day |  | 3.16
| 57601 | E101 | 1 | Month |  | 3.16
| 57602 | E102 | 1 | Year |  | 3.16
| 57603 | E103 | 1 | Hour |  | 3.16
| 57604 | E104 | 1 | Minute |  | 3.16
| 57605 | E105 | 1 | Second |  | 3.16
| 57600 | E100 | 6
E200 Hex : Action system ( Write Function only )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57856 | E200 | 1 | Action : 0xA1 : Product Configuration storage 0xB2 : Produit reset |  | 6
| 57856 | E200 | 1
E220 Hex : Value reset ( Write Function only )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57888 | E220 | 1 | Erase : These values could be combine all 0x0001 : Min/Max and AVG 4V 0x0002 : Min/Max and AVG 3U 0x0004 : Min/Max and AVG 4I 0x0008 : Min/Max and AVG F 0x0010 : Min/Max and AVG P+ 0x0020 : Min/Max and AVG P- 0x0040 : Min/Max and AVG Q+ 0x0080 : Min/Max and AVG Q- 0x0100 : Min/Max and AVG S 0x0200 : Min/Max and AVG PF 0x0400 : Min/Max and AVG THD 4V 0x0800 : Min/Max and AVG THD 3U 0x1000 : Min/Max and AVG THD 4I 0x2000 : Min/Max and AVG TIHD 4V 0x4000 : Min/Max and AVG TIHD 3U 0x8000 : Min/Max and AVG TIHD 4I |  | 3,6,16
| 57889 | E221 | 1 | Erase : These values could be combine all 0x0001 : Instantaneous Min/Max 4V 0x0002 : Instantaneous Min/Max 3U 0x0004 : Instantaneous Min/Max 4I 0x0008 : Instantaneous Min/Max F 0x0010 : Instantaneous Min/Max P+ 0x0020 : Instantaneous Min/Max P- 0x0040 : Instantaneous Min/Max Q+ 0x0080 : Instantaneous Min/Max Q- 0x0100 : Instantaneous Min/Max S 0x0200 : Instantaneous Min/Max PF 0x0400 : Instantaneous Min/Max THD 4V 0x0800 : Instantaneous Min/Max THD 3U 0x1000 : Instantaneous Min/Max THD 4I 0x2000 : Instantaneous Min/Max TIHD 4V 0x4000 : Instantaneous Min/Max TIHD 3U 0x8000 : Instantaneous Min/Max TIHD 4I |  | 3,6,16
| 57890 | E222 | 1 | Erase : 0x0001 : Ea+ 0x0002 : Er+ 0x0004 : Es 0x0008 : Ea- 0x0010 : Er- 0x0020 : Hour counter 0x0040 : All average P/Q/S 0x0080 : All events and all curves 0x0100 : All alarms |  | 3,6,16
| 57891 | E223 | 1 | Erase : These values could be combine all 0x0001 : Input pulse counter 1 0x0002 : Input pulse counter 2 0x0004 : Input pulse counter 3 0x0008 : Input pulse counter 4 0x0010 : Input pulse counter 5 0x0020 : Input pulse counter 6 0x0040 : Input pulse counter 7 0x0080 : Input pulse counter 8 0x0100 : Input pulse counter 9 0x0200 : Input pulse counter 10 |  | 3,6,16
| 57892 | E224 | 1 | Erase : These values could be combine all 0x0001 : Tariff counter 1 0x0002 : Tariff counter 2 0x0004 : Tariff counter 3 0x0008 : Tariff counter 4 0x0010 : Tariff counter 5 0x0020 : Tariff counter 6 0x0040 : Tariff counter 7 0x0080 : Tariff counter 8 |  | 3,6,16
| 57888 | E220 | 5
E300 Hex : Lock system
| #REF! | #REF! | #REF!
After having set the period ( Write at F8C0) the table F8D0 is initialized with the 10 first lastest curve date present in this period
If the date at the addresse F8F is lower than the period End Date : 1 - Set a new period 2 - Read again at F8D
F900 : Histo Alarms
The format of these tables is based on the Historical table format
| See : | Application Note : Historic
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 63744 | F900 | 1 | R1 Area |  | 6
| 63760 | F910 | 122 | R2 Area |  | 3
| 63882 | F98A
R2 area : Data Area
Read events
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 63744 | F900 | 1 | record count |  | 3
| 63745 | F901 | 1 | record size | nb words | 3
| 63746 | F902 | 120 | 15 * Alarms data record |  | 3
| 63866 | F97A | 122
Data record description
| 0 | 0 | 1 | ID : Alarm ID
| 1 | 1 | 1 | Type : 0 : State 1 : Edge 2 : System
| 2 | 2 | 1 | Severity : 0 : none 1 : information 2 : warning 3 : default
| 3 | 3 | 1 | Satus : 0 : non active 1 : active 2 : finished 3 : new & checked 4 : finished & checked
CC00 : Alarms in progress
The format of these tables is based on the Historical table format
| See : | Application Note : Historic
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 52224 | CC00 | 1 | R1 Area |  | 6
| 52240 | CC10 | 122 | R2 Area |  | 3
| 52362 | CC8A
Alarms data record
| 0 | 0 | 1 | ID : Alarm ID
| 1 | 1 | 1 | Type : 0 : State 1 : Edge 2 : System
| 2 | 2 | 1 | Severity : 0 : none 1 : information 2 : warning 3 : default
| 3 | 3 | 1 | Satus : 0 : non active 1 : active 2 : finished 3 : new & checked 4 : finished & checked
| 4 | 4 | 2 | Start Date | s since 1 jan 2000
| 6 | 6 | 2 | Duration | s
8
R2 area : Data Area
Read events
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 52240 | CC10 | 1 | record count |  | 3
| 52241 | CC11 | 1 | record size | nb words | 3
| 52242 | CC12 | 120 | 15 * Alarms data record |  | 3
| 52240 | CC10 | 122
EC700 specific tables
9000 Hex : Table Sythesis Pulse meters - Total, Partial and Custom
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 36864 | 9000 | 2 | Date & Time Current | sec. | 3
| 36866 | 9002 | 1 | Input 1 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36867 | 9003 | 1 | Input 1 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36868 | 9004 | 2 | Input 1 Weight | 1/10 of Unit | 3
| 36870 | 9006 | 4 | Input 1 Pulse meter total | Imp. (signed) | 3
| 36874 | 900A | 4 | Input 1 Pulse meter partial | Imp. (signed) | 3
| 36878 | 900E | 2 | Input 1 Pulse meter current custom time | Imp. (signed) | 3
| 36880 | 9010 | 1 | Input 2 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36881 | 9011 | 1 | Input 2 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36882 | 9012 | 2 | Input 2 Weight | 1/10 of Unit | 3
| 36884 | 9014 | 4 | Input 2 Pulse meter total | Imp. (signed) | 3
| 36888 | 9018 | 4 | Input 2 Pulse meter partial | Imp. (signed) | 3
| 36892 | 901C | 2 | Input 2 Pulse meter current custom time | Imp. (signed) | 3
| 36894 | 901E | 1 | Input 3 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36895 | 901F | 1 | Input 3 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36896 | 9020 | 2 | Input 3 Weight | 1/10 of Unit | 3
| 36898 | 9022 | 4 | Input 3 Pulse meter total | Imp. (signed) | 3
| 36902 | 9026 | 4 | Input 3 Pulse meter partial | Imp. (signed) | 3
| 36906 | 902A | 2 | Input 3 Pulse meter current custom time | Imp. (signed) | 3
| 36908 | 902C | 1 | Input 4 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36909 | 902D | 1 | Input 4 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36910 | 902E | 2 | Input 4 Weight | 1/10 of Unit | 3
| 36912 | 9030 | 4 | Input 4 Pulse meter total | Imp. (signed) | 3
| 36916 | 9034 | 4 | Input 4 Pulse meter partial | Imp. (signed) | 3
| 36920 | 9038 | 2 | Input 4 Pulse meter current custom time | Imp. (signed) | 3
| 36922 | 903A | 1 | Input 5 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36923 | 903B | 1 | Input 5 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36924 | 903C | 2 | Input 5 Weight | 1/10 of Unit | 3
| 36926 | 903E | 4 | Input 5 Pulse meter total | Imp. (signed) | 3
| 36930 | 9042 | 4 | Input 5 Pulse meter partial | Imp. (signed) | 3
| 36934 | 9046 | 2 | Input 5 Pulse meter current custom time | Imp. (signed) | 3
| 36936 | 9048 | 1 | Input 6 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36937 | 9049 | 1 | Input 6 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36938 | 904A | 2 | Input 6 Weight | 1/10 of Unit | 3
| 36940 | 904C | 4 | Input 6 Pulse meter total | Imp. (signed) | 3
| 36944 | 9050 | 4 | Input 6 Pulse meter partial | Imp. (signed) | 3
| 36948 | 9054 | 2 | Input 6 Pulse meter current custom time | Imp. (signed) | 3
| 36950 | 9056 | 1 | Input 7 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state 3 : Synchro input | Enumeration | 3
| 36951 | 9057 | 1 | Input 7 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36952 | 9058 | 2 | Input 7 Weight | 1/10 of Unit | 3
| 36954 | 905A | 4 | Input 7 Pulse meter total | Imp. (signed) | 3
| 36958 | 905E | 4 | Input 7 Pulse meter partial | Imp. (signed) | 3
| 36962 | 9062 | 2 | Input 7 Pulse meter current custom time | Imp. (signed) | 3
| 36864 | 9000 | 100
9060 Hex : Table Sythesis Pulse meters - Since last top, weekly and monthly
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 36992 | 9080 | 2 | Date & Time Current | sec. | 3
| 36994 | 9082 | 1 | Input 1 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 36995 | 9083 | 1 | Input 1 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 36996 | 9084 | 2 | Input 1 Weight | 1/10 of Unit | 3
| 36998 | 9086 | 2 | Input 1 Pulse meter current day | Imp. (signed) | 3
| 37000 | 9088 | 2 | Input 1 Pulse meter current week | Imp. (signed) | 3
| 37002 | 908A | 2 | Input 1 Pulse meter current month | Imp. (signed) | 3
| 37004 | 908C | 2 | Input 1 Pulse meter last complete period | Imp. (signed) | 3
| 37006 | 908E | 1 | Input 2 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37007 | 908F | 1 | Input 2 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37008 | 9090 | 2 | Input 2 Weight | 1/10 of Unit | 3
| 37010 | 9092 | 2 | Input 2 Pulse meter current day | Imp. (signed) | 3
| 37012 | 9094 | 2 | Input 2 Pulse meter current week | Imp. (signed) | 3
| 37014 | 9096 | 2 | Input 2 Pulse meter current month | Imp. (signed) | 3
| 37016 | 9098 | 2 | Input 2 Pulse meter last complete period | Imp. (signed) | 3
| 37018 | 909A | 1 | Input 3 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37019 | 909B | 1 | Input 3 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37020 | 909C | 2 | Input 3 Weight | 1/10 of Unit | 3
| 37022 | 909E | 2 | Input 3 Pulse meter current day | Imp. (signed) | 3
| 37024 | 90A0 | 2 | Input 3 Pulse meter current week | Imp. (signed) | 3
| 37026 | 90A2 | 2 | Input 3 Pulse meter current month | Imp. (signed) | 3
| 37028 | 90A4 | 2 | Input 3 Pulse meter last complete period | Imp. (signed) | 3
| 37030 | 90A6 | 1 | Input 4 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37031 | 90A7 | 1 | Input 4 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37032 | 90A8 | 2 | Input 4 Weight | 1/10 of Unit | 3
| 37034 | 90AA | 2 | Input 4 Pulse meter current day | Imp. (signed) | 3
| 37036 | 90AC | 2 | Input 4 Pulse meter current week | Imp. (signed) | 3
| 37038 | 90AE | 2 | Input 4 Pulse meter current month | Imp. (signed) | 3
| 37040 | 90B0 | 2 | Input 4 Pulse meter last complete period | Imp. (signed) | 3
| 37042 | 90B2 | 1 | Input 5 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37043 | 90B3 | 1 | Input 5 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37044 | 90B4 | 2 | Input 5 Weight | 1/10 of Unit | 3
| 37046 | 90B6 | 2 | Input 5 Pulse meter current day | Imp. (signed) | 3
| 37048 | 90B8 | 2 | Input 5 Pulse meter current week | Imp. (signed) | 3
| 37050 | 90BA | 2 | Input 5 Pulse meter current month | Imp. (signed) | 3
| 37052 | 90BC | 2 | Input 5 Pulse meter last complete period | Imp. (signed) | 3
| 37054 | 90BE | 1 | Input 6 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37055 | 90BF | 1 | Input 6 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37056 | 90C0 | 2 | Input 6 Weight | 1/10 of Unit | 3
| 37058 | 90C2 | 2 | Input 6 Pulse meter current day | Imp. (signed) | 3
| 37060 | 90C4 | 2 | Input 6 Pulse meter current week | Imp. (signed) | 3
| 37062 | 90C6 | 2 | Input 6 Pulse meter current month | Imp. (signed) | 3
| 37064 | 90C8 | 2 | Input 6 Pulse meter last complete period | Imp. (signed) | 3
| 37066 | 90CA | 1 | Input 7 Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state 3 : Synchro input | Enumeration | 3
| 37067 | 90CB | 1 | Input 7 Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37068 | 90CC | 2 | Input 7 Weight | 1/10 of Unit | 3
| 37070 | 90CE | 2 | Input 7 Pulse meter current day | Imp. (signed) | 3
| 37072 | 90D0 | 2 | Input 7 Pulse meter current week | Imp. (signed) | 3
| 37074 | 90D2 | 2 | Input 7 Pulse meter current month | Imp. (signed) | 3
| 37076 | 90D4 | 2 | Input 7 Pulse meter last complete period | Imp. (signed) | 3
| 36992 | 9080 | 86
90E0 Hex : Custom meters commands
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37088 | 90E0 | 1 | Input 1 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37089 | 90E1 | 1 | Input 2 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37090 | 90E2 | 1 | Input 3 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37091 | 90E3 | 1 | Input 4 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37092 | 90E4 | 1 | Input 5 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37093 | 90E5 | 1 | Input 6 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37094 | 90E6 | 1 | Input 7 custom meter 0 : Stop 1 : Start | Enumeration | 3, 6, 16
| 37088 | 90E0 | 7
90F0 Hex : Top synchro command
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37104 | 90F0 | 1 | Top synchro command 1 : New top | Enumeration | 6
| 37104 | 90F0 | 1
9100 Hex : Table indexes input by input
Input 1
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37120 | 9100 | 2 | Date & Time Current | sec. | 3
| 37122 | 9102 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37123 | 9103 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37124 | 9104 | 1 | Integration Time | min. | 3
| 37125 | 9105 | 2 | Weight | 1/10 of Unit | 3
| 37127 | 9107 | 2 | Currency conversion | 1/1000000 | 3
| 37129 | 9109 | 2 | Date & Time of partial meter start | / | 3
| 37131 | 910B | 4 | Pulse meter total | Imp. (signed) | 3
| 37135 | 910F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37139 | 9113 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37141 | 9115 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37143 | 9117 | 2 | Pulse meter last complete | Imp. (signed)
| 37145 | 9119 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37147 | 911B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37149 | 911D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37151 | 911F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37153 | 9121 | 1 | Number of valid meters for previous days | / | 3
| 37154 | 9122 | 1 | Number of valid meters for previous weeks | / | 3
| 37155 | 9123 | 1 | Number of valid meters for previous months | / | 3
| 37156 | 9124 | 1 | Number of valid meters for previous years | / | 3
| 37157 | 9125 | 1 | Number of valid meters for previous custom | / | 3
| 37158 | 9126 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37160 | 9128 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37162 | 912A | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37164 | 912C | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37166 | 912E | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37168 | 9130 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37170 | 9132 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37172 | 9134 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37174 | 9136 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37176 | 9138 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37178 | 913A | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37180 | 913C | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37182 | 913E | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37184 | 9140 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37186 | 9142 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37188 | 9144 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37190 | 9146 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37192 | 9148 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37194 | 914A | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37196 | 914C | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37198 | 914E | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37200 | 9150 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37202 | 9152 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37204 | 9154 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37206 | 9156 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37208 | 9158 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37210 | 915A | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37212 | 915C | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37214 | 915E | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37216 | 9160 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37218 | 9162 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37220 | 9164 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37120 | 9100 | 102
Input 2
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37248 | 9180 | 2 | Date & Time Current | sec. | 3
| 37250 | 9182 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37251 | 9183 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37252 | 9184 | 1 | Integration Time | min. | 3
| 37253 | 9185 | 2 | Weight | 1/10 of Unit | 3
| 37255 | 9187 | 2 | Currency conversion | 1/1000000 | 3
| 37257 | 9189 | 2 | Date & Time of partial meter start | / | 3
| 37259 | 918B | 4 | Pulse meter total | Imp. (signed) | 3
| 37263 | 918F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37267 | 9193 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37269 | 9195 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37271 | 9197 | 2 | Pulse meter last complete | Imp. (signed)
| 37273 | 9199 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37275 | 919B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37277 | 919D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37279 | 919F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37281 | 91A1 | 1 | Number of valid meters for previous days | / | 3
| 37282 | 91A2 | 1 | Number of valid meters for previous weeks | / | 3
| 37283 | 91A3 | 1 | Number of valid meters for previous months | / | 3
| 37284 | 91A4 | 1 | Number of valid meters for previous years | / | 3
| 37285 | 91A5 | 1 | Number of valid meters for previous custom | / | 3
| 37286 | 91A6 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37288 | 91A8 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37290 | 91AA | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37292 | 91AC | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37294 | 91AE | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37296 | 91B0 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37298 | 91B2 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37300 | 91B4 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37302 | 91B6 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37304 | 91B8 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37306 | 91BA | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37308 | 91BC | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37310 | 91BE | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37312 | 91C0 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37314 | 91C2 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37316 | 91C4 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37318 | 91C6 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37320 | 91C8 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37322 | 91CA | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37324 | 91CC | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37326 | 91CE | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37328 | 91D0 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37330 | 91D2 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37332 | 91D4 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37334 | 91D6 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37336 | 91D8 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37338 | 91DA | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37340 | 91DC | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37342 | 91DE | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37344 | 91E0 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37346 | 91E2 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37348 | 91E4 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37248 | 9180 | 102
Input 3
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37376 | 9200 | 2 | Date & Time Current | sec. | 3
| 37378 | 9202 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37379 | 9203 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37380 | 9204 | 1 | Integration Time | min. | 3
| 37381 | 9205 | 2 | Weight | 1/10 of Unit | 3
| 37383 | 9207 | 2 | Currency conversion | 1/1000000 | 3
| 37385 | 9209 | 2 | Date & Time of partial meter start | / | 3
| 37387 | 920B | 4 | Pulse meter total | Imp. (signed) | 3
| 37391 | 920F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37395 | 9213 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37397 | 9215 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37399 | 9217 | 2 | Pulse meter last complete | Imp. (signed)
| 37401 | 9219 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37403 | 921B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37405 | 921D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37407 | 921F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37409 | 9221 | 1 | Number of valid meters for previous days | / | 3
| 37410 | 9222 | 1 | Number of valid meters for previous weeks | / | 3
| 37411 | 9223 | 1 | Number of valid meters for previous months | / | 3
| 37412 | 9224 | 1 | Number of valid meters for previous years | / | 3
| 37413 | 9225 | 1 | Number of valid meters for previous custom | / | 3
| 37414 | 9226 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37416 | 9228 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37418 | 922A | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37420 | 922C | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37422 | 922E | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37424 | 9230 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37426 | 9232 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37428 | 9234 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37430 | 9236 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37432 | 9238 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37434 | 923A | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37436 | 923C | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37438 | 923E | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37440 | 9240 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37442 | 9242 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37444 | 9244 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37446 | 9246 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37448 | 9248 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37450 | 924A | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37452 | 924C | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37454 | 924E | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37456 | 9250 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37458 | 9252 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37460 | 9254 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37462 | 9256 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37464 | 9258 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37466 | 925A | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37468 | 925C | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37470 | 925E | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37472 | 9260 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37474 | 9262 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37476 | 9264 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37376 | 9200 | 102
Input 4
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37504 | 9280 | 2 | Date & Time Current | sec. | 3
| 37506 | 9282 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37507 | 9283 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37508 | 9284 | 1 | Integration Time | min. | 3
| 37509 | 9285 | 2 | Weight | 1/10 of Unit | 3
| 37511 | 9287 | 2 | Currency conversion | 1/1000000 | 3
| 37513 | 9289 | 2 | Date & Time of partial meter start | / | 3
| 37515 | 928B | 4 | Pulse meter total | Imp. (signed) | 3
| 37519 | 928F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37523 | 9293 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37525 | 9295 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37527 | 9297 | 2 | Pulse meter last complete | Imp. (signed)
| 37529 | 9299 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37531 | 929B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37533 | 929D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37535 | 929F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37537 | 92A1 | 1 | Number of valid meters for previous days | / | 3
| 37538 | 92A2 | 1 | Number of valid meters for previous weeks | / | 3
| 37539 | 92A3 | 1 | Number of valid meters for previous months | / | 3
| 37540 | 92A4 | 1 | Number of valid meters for previous years | / | 3
| 37541 | 92A5 | 1 | Number of valid meters for previous custom | / | 3
| 37542 | 92A6 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37544 | 92A8 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37546 | 92AA | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37548 | 92AC | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37550 | 92AE | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37552 | 92B0 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37554 | 92B2 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37556 | 92B4 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37558 | 92B6 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37560 | 92B8 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37562 | 92BA | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37564 | 92BC | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37566 | 92BE | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37568 | 92C0 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37570 | 92C2 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37572 | 92C4 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37574 | 92C6 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37576 | 92C8 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37578 | 92CA | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37580 | 92CC | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37582 | 92CE | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37584 | 92D0 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37586 | 92D2 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37588 | 92D4 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37590 | 92D6 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37592 | 92D8 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37594 | 92DA | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37596 | 92DC | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37598 | 92DE | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37600 | 92E0 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37602 | 92E2 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37604 | 92E4 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37504 | 9280 | 102
Input 5
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37632 | 9300 | 2 | Date & Time Current | sec. | 3
| 37634 | 9302 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37635 | 9303 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37636 | 9304 | 1 | Integration Time | min. | 3
| 37637 | 9305 | 2 | Weight | 1/10 of Unit | 3
| 37639 | 9307 | 2 | Currency conversion | 1/1000000 | 3
| 37641 | 9309 | 2 | Date & Time of partial meter start | / | 3
| 37643 | 930B | 4 | Pulse meter total | Imp. (signed) | 3
| 37647 | 930F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37651 | 9313 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37653 | 9315 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37655 | 9317 | 2 | Pulse meter last complete | Imp. (signed)
| 37657 | 9319 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37659 | 931B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37661 | 931D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37663 | 931F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37665 | 9321 | 1 | Number of valid meters for previous days | / | 3
| 37666 | 9322 | 1 | Number of valid meters for previous weeks | / | 3
| 37667 | 9323 | 1 | Number of valid meters for previous months | / | 3
| 37668 | 9324 | 1 | Number of valid meters for previous years | / | 3
| 37669 | 9325 | 1 | Number of valid meters for previous custom | / | 3
| 37670 | 9326 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37672 | 9328 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37674 | 932A | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37676 | 932C | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37678 | 932E | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37680 | 9330 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37682 | 9332 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37684 | 9334 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37686 | 9336 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37688 | 9338 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37690 | 933A | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37692 | 933C | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37694 | 933E | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37696 | 9340 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37698 | 9342 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37700 | 9344 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37702 | 9346 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37704 | 9348 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37706 | 934A | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37708 | 934C | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37710 | 934E | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37712 | 9350 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37714 | 9352 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37716 | 9354 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37718 | 9356 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37720 | 9358 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37722 | 935A | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37724 | 935C | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37726 | 935E | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37728 | 9360 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37730 | 9362 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37732 | 9364 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37632 | 9300 | 102
Input 6
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37760 | 9380 | 2 | Date & Time Current | sec. | 3
| 37762 | 9382 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state | Enumeration | 3
| 37763 | 9383 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37764 | 9384 | 1 | Integration Time | min. | 3
| 37765 | 9385 | 2 | Weight | 1/10 of Unit | 3
| 37767 | 9387 | 2 | Currency conversion | 1/1000000 | 3
| 37769 | 9389 | 2 | Date & Time of partial meter start | / | 3
| 37771 | 938B | 4 | Pulse meter total | Imp. (signed) | 3
| 37775 | 938F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37779 | 9393 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37781 | 9395 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37783 | 9397 | 2 | Pulse meter last complete | Imp. (signed)
| 37785 | 9399 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37787 | 939B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37789 | 939D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37791 | 939F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37793 | 93A1 | 1 | Number of valid meters for previous days | / | 3
| 37794 | 93A2 | 1 | Number of valid meters for previous weeks | / | 3
| 37795 | 93A3 | 1 | Number of valid meters for previous months | / | 3
| 37796 | 93A4 | 1 | Number of valid meters for previous years | / | 3
| 37797 | 93A5 | 1 | Number of valid meters for previous custom | / | 3
| 37798 | 93A6 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37800 | 93A8 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37802 | 93AA | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37804 | 93AC | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37806 | 93AE | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37808 | 93B0 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37810 | 93B2 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37812 | 93B4 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37814 | 93B6 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37816 | 93B8 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37818 | 93BA | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37820 | 93BC | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37822 | 93BE | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37824 | 93C0 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37826 | 93C2 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37828 | 93C4 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37830 | 93C6 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37832 | 93C8 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37834 | 93CA | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37836 | 93CC | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37838 | 93CE | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37840 | 93D0 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37842 | 93D2 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37844 | 93D4 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37846 | 93D6 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37848 | 93D8 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37850 | 93DA | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37852 | 93DC | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37854 | 93DE | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37856 | 93E0 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37858 | 93E2 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37860 | 93E4 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37760 | 9380 | 102
Input 7
| Adresse Déc. | Adresse Hex. | Nb de mots | Libellé | Unité | Function
| 37888 | 9400 | 2 | Date & Time Current | sec. | 3
| 37890 | 9402 | 1 | Input Mode : 0 : Disabled 1 : Pulse meter 2 : Logical state 3 : Synchro input | Enumeration | 3
| 37891 | 9403 | 1 | Input Unit 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | Enumeration | 3
| 37892 | 9404 | 1 | Integration Time | min. | 3
| 37893 | 9405 | 2 | Weight | 1/10 of Unit | 3
| 37895 | 9407 | 2 | Currency conversion | 1/1000000 | 3
| 37897 | 9409 | 2 | Date & Time of partial meter start | / | 3
| 37899 | 940B | 4 | Pulse meter total | Imp. (signed) | 3
| 37903 | 940F | 4 | Pulse meter partial | Imp. (signed) | 3
| 37907 | 9413 | 2 | Pulse meter current custom time | Imp. (signed) | 3
| 37909 | 9415 | 2 | Pulse meter last (since last Top) | Imp. (signed) | 3
| 37911 | 9417 | 2 | Pulse meter last complete | Imp. (signed)
| 37913 | 9419 | 2 | Pulse meter current day | Imp. (signed) | 3
| 37915 | 941B | 2 | Pulse meter current week | Imp. (signed) | 3
| 37917 | 941D | 2 | Pulse meter current month | Imp. (signed) | 3
| 37919 | 941F | 2 | Pulse meter current year | Imp. (signed) | 3
| 37921 | 9421 | 1 | Number of valid meters for previous days | / | 3
| 37922 | 9422 | 1 | Number of valid meters for previous weeks | / | 3
| 37923 | 9423 | 1 | Number of valid meters for previous months | / | 3
| 37924 | 9424 | 1 | Number of valid meters for previous years | / | 3
| 37925 | 9425 | 1 | Number of valid meters for previous custom | / | 3
| 37926 | 9426 | 2 | Pulse meter previous days d-1 | Imp. (signed) | 3
| 37928 | 9428 | 2 | Pulse meter previous days d-2 | Imp. (signed) | 3
| 37930 | 942A | 2 | Pulse meter previous days d-3 | Imp. (signed) | 3
| 37932 | 942C | 2 | Pulse meter previous days d-4 | Imp. (signed) | 3
| 37934 | 942E | 2 | Pulse meter previous days d-5 | Imp. (signed) | 3
| 37936 | 9430 | 2 | Pulse meter previous days d-6 | Imp. (signed) | 3
| 37938 | 9432 | 2 | Pulse meter previous days d-7 | Imp. (signed) | 3
| 37940 | 9434 | 2 | Pulse meter previous weeks w-1 | Imp. (signed) | 3
| 37942 | 9436 | 2 | Pulse meter previous weeks w-2 | Imp. (signed) | 3
| 37944 | 9438 | 2 | Pulse meter previous weeks w-3 | Imp. (signed) | 3
| 37946 | 943A | 2 | Pulse meter previous weeks w-4 | Imp. (signed) | 3
| 37948 | 943C | 2 | Pulse meter previous weeks w-5 | Imp. (signed) | 3
| 37950 | 943E | 2 | Pulse meter previous months m-1 | Imp. (signed) | 3
| 37952 | 9440 | 2 | Pulse meter previous months m-2 | Imp. (signed) | 3
| 37954 | 9442 | 2 | Pulse meter previous months m-3 | Imp. (signed) | 3
| 37956 | 9444 | 2 | Pulse meter previous months m-4 | Imp. (signed) | 3
| 37958 | 9446 | 2 | Pulse meter previous months m-5 | Imp. (signed) | 3
| 37960 | 9448 | 2 | Pulse meter previous months m-6 | Imp. (signed) | 3
| 37962 | 944A | 2 | Pulse meter previous months m-7 | Imp. (signed) | 3
| 37964 | 944C | 2 | Pulse meter previous months m-8 | Imp. (signed) | 3
| 37966 | 944E | 2 | Pulse meter previous months m-9 | Imp. (signed) | 3
| 37968 | 9450 | 2 | Pulse meter previous months m-10 | Imp. (signed) | 3
| 37970 | 9452 | 2 | Pulse meter previous months m-11 | Imp. (signed) | 3
| 37972 | 9454 | 2 | Pulse meter previous months m-12 | Imp. (signed) | 3
| 37974 | 9456 | 2 | Pulse meter previous year | Imp. (signed) | 3
| 37976 | 9458 | 2 | Pulse meter previous custom c-1 | Imp. (signed) | 3
| 37978 | 945A | 2 | Pulse meter previous custom c-2 | Imp. (signed) | 3
| 37980 | 945C | 2 | Pulse meter previous custom c-3 | Imp. (signed) | 3
| 37982 | 945E | 2 | Pulse meter previous custom c-4 | Imp. (signed) | 3
| 37984 | 9460 | 2 | Pulse meter previous custom c-5 | Imp. (signed) | 3
| 37986 | 9462 | 2 | Pulse meter previous custom c-6 | Imp. (signed) | 3
| 37988 | 9464 | 2 | Pulse meter previous custom c-7 | Imp. (signed) | 3
| 37888 | 9400 | 102
9500 Hex : Table Inputs load curves
Example : Logical inputs load curves
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38144 | 9500 | 1 | R1 Area |  | 6
| 38160 | 9510 | 122 | R2 Area |  | 3
| 38282 | 958A
R2 area : Data Area
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
Header | 38160 | 9510 | 1 | Record count ( Maximum 29 ) |  | 3
| 38161 | 9511 | 1 | Record size = 4 see below the data record description | Nb Words | 3
| 38162 | 9512 | 1 | Integration period | second | 3
| 38163 | 9513 | 1 | Physical Unit | Base Unit 0 : W 1 : W 2 : var 3 : var 4 : VA 5 : None 6 : J 7 : Pulse 8 : m3 9 : Nm3 20 : kW 22 : kVAr 24 : kVA 26 : kJ 27 : kilo-Pulse | 3
| 38164 | 9514 | 1 | Numerator Rate |  | 3
| 38165 | 9515 | 1 | Denominator Rate |  | 3
Data Buffer | 38166 | 9516 | 116 | Records (x29) see below the description |  | 3
| 38282 | 958A | 122
Data record description
|  |  | Word Count | Description | Unit
|  |  | 2 | Date | second since 1st jan 2000
|  |  | 1 | Full/incomplete period | 0 : full integration period 1 : incomplete integration period
|  |  | 1 | Value | Unit = Base Unit * Numerator Rate / Denominator Rate
4
the power value in Watt = Value * Numerator / Denominator
9500 Hex : Input 1
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38144 | 9500 | 1 | R1 Area |  | 6
| 38160 | 9510 | 122 | R2 Area |  | 3
| 38282 | 958A
9590 Hex : Input 2
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38288 | 9590 | 1 | R1 Area |  | 6
| 38304 | 95A0 | 122 | R2 Area |  | 3
| 38426 | 961A
9620 Hex : Input 3
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38432 | 9620 | 1 | R1 Area |  | 6
| 38448 | 9630 | 122 | R2 Area |  | 3
| 38570 | 96AA
96B0 Hex : Input 4
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38576 | 96B0 | 1 | R1 Area |  | 6
| 38592 | 96C0 | 122 | R2 Area |  | 3
| 38714 | 973A
9740 Hex : Input 5
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38720 | 9740 | 1 | R1 Area |  | 6
| 38736 | 9750 | 122 | R2 Area |  | 3
| 38858 | 97CA
97D0 Hex : Input 6
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 38864 | 97D0 | 1 | R1 Area |  | 6
| 38880 | 97E0 | 122 | R2 Area |  | 3
| 39002 | 985A
9860 Hex : Input 7
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39008 | 9860 | 1 | R1 Area |  | 6
| 39024 | 9870 | 122 | R2 Area |  | 3
| 39146 | 98EA
9B00 Hex : Table Settings for logical inputs, ouputs
Input 1
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39680 | 9B00 | 5 | Name | / | 3, 6, 16
| 39685 | 9B05 | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39686 | 9B06 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39687 | 9B07 | 1 | Delay | 100ms | 3, 6, 16
| 39688 | 9B08 | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39690 | 9B0A | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39691 | 9B0B | 1 | Integration Time | (* base) min | 3, 6, 16
| 39692 | 9B0C | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39693 | 9B0D | 1 | Time On Off | 10ms | 3, 6, 16
| 39694 | 9B0E | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39695 | 9B0F | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39697 | 9B11 | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39698 | 9B12 | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39699 | 9B13 | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39703 | 9B17 | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39680 | 9B00 | 27
Input 2
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39707 | 9B1B | 5 | Name | / | 3, 6, 16
| 39712 | 9B20 | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39713 | 9B21 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39714 | 9B22 | 1 | Delay | 100ms | 3, 6, 16
| 39715 | 9B23 | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39717 | 9B25 | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39718 | 9B26 | 1 | Integration Time | (* base) min | 3, 6, 16
| 39719 | 9B27 | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39720 | 9B28 | 1 | Time On Off | 10ms | 3, 6, 16
| 39721 | 9B29 | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39722 | 9B2A | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39724 | 9B2C | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39725 | 9B2D | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39726 | 9B2E | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39730 | 9B32 | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39707 | 9B1B | 27
Input 3
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39734 | 9B36 | 5 | Name | / | 3, 6, 16
| 39739 | 9B3B | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39740 | 9B3C | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39741 | 9B3D | 1 | Delay | 100ms | 3, 6, 16
| 39742 | 9B3E | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39744 | 9B40 | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39745 | 9B41 | 1 | Integration Time | (* base) min | 3, 6, 16
| 39746 | 9B42 | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39747 | 9B43 | 1 | Time On Off | 10ms | 3, 6, 16
| 39748 | 9B44 | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39749 | 9B45 | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39751 | 9B47 | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39752 | 9B48 | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39753 | 9B49 | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39757 | 9B4D | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39734 | 9B36 | 27
Input 4
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39761 | 9B51 | 5 | Name | / | 3, 6, 16
| 39766 | 9B56 | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39767 | 9B57 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39768 | 9B58 | 1 | Delay | 100ms | 3, 6, 16
| 39769 | 9B59 | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39771 | 9B5B | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39772 | 9B5C | 1 | Integration Time | (* base) min | 3, 6, 16
| 39773 | 9B5D | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39774 | 9B5E | 1 | Time On Off | 10ms | 3, 6, 16
| 39775 | 9B5F | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39776 | 9B60 | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39778 | 9B62 | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39779 | 9B63 | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39780 | 9B64 | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39784 | 9B68 | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39761 | 9B51 | 27
Input 5
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39788 | 9B6C | 5 | Name | / | 3, 6, 16
| 39793 | 9B71 | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39794 | 9B72 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39795 | 9B73 | 1 | Delay | 100ms | 3, 6, 16
| 39796 | 9B74 | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39798 | 9B76 | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39799 | 9B77 | 1 | Integration Time | (* base) min | 3, 6, 16
| 39800 | 9B78 | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39801 | 9B79 | 1 | Time On Off | 10ms | 3, 6, 16
| 39802 | 9B7A | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39803 | 9B7B | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39805 | 9B7D | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39806 | 9B7E | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39807 | 9B7F | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39811 | 9B83 | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39788 | 9B6C | 27
Input 6
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39815 | 9B87 | 5 | Name | / | 3, 6, 16
| 39820 | 9B8C | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input | Enumeration | 3, 6, 16
| 39821 | 9B8D | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39822 | 9B8E | 1 | Delay | 100ms | 3, 6, 16
| 39823 | 9B8F | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39825 | 9B91 | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39826 | 9B92 | 1 | Integration Time | (* base) min | 3, 6, 16
| 39827 | 9B93 | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39828 | 9B94 | 1 | Time On Off | 10ms | 3, 6, 16
| 39829 | 9B95 | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39830 | 9B96 | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39832 | 9B98 | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39833 | 9B99 | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39834 | 9B9A | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39838 | 9B9E | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39815 | 9B87 | 27
Input 7
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39842 | 9BA2 | 5 | Name | / | 3, 6, 16
| 39847 | 9BA7 | 1 | Mode : 0x00 : Disabled 0x01 : Pulse meter 0x02 : Logical input 0x03 : Synchro Input | Enumeration | 3, 6, 16
| 39848 | 9BA8 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39849 | 9BA9 | 1 | Delay | 100ms | 3, 6, 16
| 39850 | 9BAA | 2 | Weight | 1/10 of Unit | 3, 6, 16
| 39852 | 9BAC | 1 | Unit : 9 : None 0 : Wh 1 : Varh 2 : VAh 3 : m3 4 : Nm3 5 : J 10 : kWh 11 : kVarh 12 : kVAh 13 : km3 14 : kNm3 15 : kJ 20 : MWh 21 : MVarh 22 : MVAh 23 : Mm3 24 : MNm3 25 : MJ | / | 3, 6, 16
| 39853 | 9BAD | 1 | Integration Time | (* base) min | 3, 6, 16
| 39854 | 9BAE | 1 | Synchro Type : 0x00 : RTC 0x01 : external | Enumeration | 3, 6, 16
| 39855 | 9BAF | 1 | Time On Off | 10ms | 3, 6, 16
| 39856 | 9BB0 | 1 | Currency Conversion Enabled 0 : Disabled 1 : Enabled | Enumeration | 3, 6, 16
| 39857 | 9BB1 | 2 | Currency Conversion rate | 1/1000000 | 3, 6, 16
| 39859 | 9BB3 | 1 | Custom Meter Mode : 0x00 : Non active 0x01 : RTC 0x02 : On COM 0x03 : On Input1 active 0x04 : On Input2 active 0x05 : On Input3 active 0x06 : On Input4 active 0x07 : On Input5 active 0x08 : On Input6 active 0x09 : On Input7 active | Enumeration | 3, 6, 16
| 39860 | 9BB4 | 1 | Custom Meter Frequency : 0x00 : daily 0x01 : weekly 0x02 : monthly 0x03 : yearly 0x04 : non cyclic | Enumeration | 3, 6, 16
| 39861 | 9BB5 | 4 | Custom Meter Start Date Time | / | 3, 6, 16
| 39865 | 9BB9 | 4 | Custom Meter End Date Time | / | 3, 6, 16
| 39842 | 9BA2 | 27
All inputs, Advanced
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39869 | 9BBD | 1 | Load Curves Base Integration Time | min | 3, 6, 16
| 39870 | 9BBE | 2 | Daily Meter Start Time: [0] : hh - hours [1] : mm - minutes [2] : ss - seconds [3] : xx - don't care | / | 3, 6, 16
| 39872 | 9BC0 | 1 | External Synchro Type : 0x00 : Disabled 0x01 : Input 7 0x02 : COM | Enumeration | 3, 6, 16
| 39873 | 9BC1 | 1 | External Synchro Period | min | 3, 6, 16
| 39874 | 9BC2 | 1 | Currency unit: 0 : Euro 1 : US Dollar 2 : GB pound 3 : Yuan 4 : Other | Enumeration | 3, 6, 16
| 39869 | 9BBD | 6
Output 1
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 39875 | 9BC3 | 5 | Name |  | 3, 6, 16
| 39880 | 9BC8 | 1 | Affectation (ID) | Enumeration | 3, 6, 16
| 39881 | 9BC9 | 1 | Type : 0x00 : NO 0x01 : NC | Enumeration | 3, 6, 16
| 39882 | 9BCA | 1 | Delay | 100ms | 3, 6, 16
| 39875 | 9BC3 | 8
203
9D00 Hex : Table Settings for 10 event objects
Event 1
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40192 | 9D00 | 5 | Name | / | 3, 6, 16
| 40197 | 9D05 | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40198 | 9D06 | 1 | Operand1 | Enumeration | 3, 6, 16
| 40199 | 9D07 | 1 | Operand2 | Enumeration | 3, 6, 16
| 40200 | 9D08 | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40201 | 9D09 | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40202 | 9D0A | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40203 | 9D0B | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40204 | 9D0C | 1 | AnaValHyst | / | 3, 6, 16
| 40205 | 9D0D | 2 | AnaValLow | / | 3, 6, 16
| 40207 | 9D0F | 2 | AnaValHigh | / | 3, 6, 16
| 40192 | 9D00 | 17
Event 2
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40209 | 9D11 | 5 | Name | / | 3, 6, 16
| 40214 | 9D16 | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40215 | 9D17 | 1 | Operand1 | Enumeration | 3, 6, 16
| 40216 | 9D18 | 1 | Operand2 | Enumeration | 3, 6, 16
| 40217 | 9D19 | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40218 | 9D1A | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40219 | 9D1B | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40220 | 9D1C | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40221 | 9D1D | 1 | AnaValHyst | / | 3, 6, 16
| 40222 | 9D1E | 2 | AnaValLow | / | 3, 6, 16
| 40224 | 9D20 | 2 | AnaValHigh | / | 3, 6, 16
| 40209 | 9D11 | 17
Event 3
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40226 | 9D22 | 5 | Name | / | 3, 6, 16
| 40231 | 9D27 | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | / | 3, 6, 16
| 40232 | 9D28 | 1 | Operand1 | / | 3, 6, 16
| 40233 | 9D29 | 1 | Operand2 | / | 3, 6, 16
| 40234 | 9D2A | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | / | 3, 6, 16
| 40235 | 9D2B | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | / | 3, 6, 16
| 40236 | 9D2C | 1 | Combination mode : 0x00 : OR 0x01 : AND | / | 3, 6, 16
| 40237 | 9D2D | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | / | 3, 6, 16
| 40238 | 9D2E | 1 | AnaValHyst | / | 3, 6, 16
| 40239 | 9D2F | 2 | AnaValLow | / | 3, 6, 16
| 40241 | 9D31 | 2 | AnaValHigh | / | 3, 6, 16
| 40226 | 9D22 | 17
Event 4
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40243 | 9D33 | 5 | Name | / | 3, 6, 16
| 40248 | 9D38 | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40249 | 9D39 | 1 | Operand1 | Enumeration | 3, 6, 16
| 40250 | 9D3A | 1 | Operand2 | Enumeration | 3, 6, 16
| 40251 | 9D3B | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40252 | 9D3C | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40253 | 9D3D | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40254 | 9D3E | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40255 | 9D3F | 1 | AnaValHyst | / | 3, 6, 16
| 40256 | 9D40 | 2 | AnaValLow | / | 3, 6, 16
| 40258 | 9D42 | 2 | AnaValHigh | / | 3, 6, 16
| 40243 | 9D33 | 17
Event 5
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40260 | 9D44 | 5 | Name | / | 3, 6, 16
| 40265 | 9D49 | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40266 | 9D4A | 1 | Operand1 | Enumeration | 3, 6, 16
| 40267 | 9D4B | 1 | Operand2 | Enumeration | 3, 6, 16
| 40268 | 9D4C | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40269 | 9D4D | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40270 | 9D4E | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40271 | 9D4F | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40272 | 9D50 | 1 | AnaValHyst | / | 3, 6, 16
| 40273 | 9D51 | 2 | AnaValLow | / | 3, 6, 16
| 40275 | 9D53 | 2 | AnaValHigh | / | 3, 6, 16
| 40260 | 9D44 | 17
Event 6
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40277 | 9D55 | 5 | Name | / | 3, 6, 16
| 40282 | 9D5A | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40283 | 9D5B | 1 | Operand1 | Enumeration | 3, 6, 16
| 40284 | 9D5C | 1 | Operand2 | Enumeration | 3, 6, 16
| 40285 | 9D5D | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40286 | 9D5E | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40287 | 9D5F | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40288 | 9D60 | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40289 | 9D61 | 1 | AnaValHyst | / | 3, 6, 16
| 40290 | 9D62 | 2 | AnaValLow | / | 3, 6, 16
| 40292 | 9D64 | 2 | AnaValHigh | / | 3, 6, 16
| 40277 | 9D55 | 17
Event 7
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40294 | 9D66 | 5 | Name | / | 3, 6, 16
| 40299 | 9D6B | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40300 | 9D6C | 1 | Operand1 | Enumeration | 3, 6, 16
| 40301 | 9D6D | 1 | Operand2 | Enumeration | 3, 6, 16
| 40302 | 9D6E | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40303 | 9D6F | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40304 | 9D70 | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40305 | 9D71 | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40306 | 9D72 | 1 | AnaValHyst | / | 3, 6, 16
| 40307 | 9D73 | 2 | AnaValLow | / | 3, 6, 16
| 40309 | 9D75 | 2 | AnaValHigh | / | 3, 6, 16
| 40294 | 9D66 | 17
Event 8
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40311 | 9D77 | 5 | Name | / | 3, 6, 16
| 40316 | 9D7C | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40317 | 9D7D | 1 | Operand1 | Enumeration | 3, 6, 16
| 40318 | 9D7E | 1 | Operand2 | Enumeration | 3, 6, 16
| 40319 | 9D7F | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40320 | 9D80 | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40321 | 9D81 | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40322 | 9D82 | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40323 | 9D83 | 1 | AnaValHyst | / | 3, 6, 16
| 40324 | 9D84 | 2 | AnaValLow | / | 3, 6, 16
| 40326 | 9D86 | 2 | AnaValHigh | / | 3, 6, 16
| 40311 | 9D77 | 17
Event 9
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40328 | 9D88 | 5 | Name | / | 3, 6, 16
| 40333 | 9D8D | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40334 | 9D8E | 1 | Operand1 | Enumeration | 3, 6, 16
| 40335 | 9D8F | 1 | Operand2 | Enumeration | 3, 6, 16
| 40336 | 9D90 | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40337 | 9D91 | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40338 | 9D92 | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40339 | 9D93 | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40340 | 9D94 | 1 | AnaValHyst | / | 3, 6, 16
| 40341 | 9D95 | 2 | AnaValLow | / | 3, 6, 16
| 40343 | 9D97 | 2 | AnaValHigh | / | 3, 6, 16
| 40328 | 9D88 | 17
Event 10
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40345 | 9D99 | 5 | Name | / | 3, 6, 16
| 40350 | 9D9E | 1 | Mode : 0x00 : Disabled 0x01 : Logical state 0x02 : Analogical value 0x03 : Combination | Enumeration | 3, 6, 16
| 40351 | 9D9F | 1 | Operand1 | Enumeration | 3, 6, 16
| 40352 | 9DA0 | 1 | Operand2 | Enumeration | 3, 6, 16
| 40353 | 9DA1 | 1 | Severity : 0x00 : None 0x01 : Information 0x02 : Warning 0x03 : Default | Enumeration | 3, 6, 16
| 40354 | 9DA2 | 1 | Logical mode : 0x00 : Low state 0x01 : High state 0x02 : Falling edge 0x03 : Rising edge 0x04 : Both falling & rising edge | Enumeration | 3, 6, 16
| 40355 | 9DA3 | 1 | Combination mode : 0x00 : OR 0x01 : AND | Enumeration | 3, 6, 16
| 40356 | 9DA4 | 1 | Analogical value comparison type : 0x00 : Low & High comparison 0x01 : Only high 0x02 : Only low 0x03 : Match with high level on rising 0x04 : Match with low level on falling | Enumeration | 3, 6, 16
| 40357 | 9DA5 | 1 | AnaValHyst | / | 3, 6, 16
| 40358 | 9DA6 | 2 | AnaValLow | / | 3, 6, 16
| 40360 | 9DA8 | 2 | AnaValHigh | / | 3, 6, 16
| 40345 | 9D99 | 17
9E00 Hex : Table Settings for communication
JBUS on RS485
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40448 | 9E00 | 1 | Address | / | 3, 6, 16
| 40449 | 9E01 | 1 | Auto Detection : 0 = NO 1 = YES | Enumeration | 3, 6, 16
| 40450 | 9E02 | 1 | Baud Rate : 3 = 9600 bps 4 = 19200 bps 5 = 38400 bps | Enumeration | 3, 6, 16
| 40451 | 9E03 | 1 | Parity : 0 = none 1 = even 2 = odd | Enumeration | 3, 6, 16
| 40452 | 9E04 | 1 | Stop bit number : 0 = 1 stop bit 1 = 2 stop bits | Enumeration | 3, 6, 16
| 40448 | 9E00 | 5
9E20 Hex : Table HMI settings
HMI
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40480 | 9E20 | 5 | Name | / | 3, 6, 16
| 40485 | 9E25 | 1 | Language 0 : English 1 : French | Enumeration | 3, 6, 16
| 40486 | 9E26 | 1 | Contrast | / | 3, 6, 16
| 40487 | 9E27 | 1 | Backlight intensity | / | 3, 6, 16
| 40488 | 9E28 | 1 | Backlight timeout | min | 3, 6, 16
| 40489 | 9E29 | 1 | Default Menu | / | 3, 6, 16
| 40490 | 9E2A | 1 | Default Screen | / | 3, 6, 16
| 40480 | 9E20 | 11
9F00 Hex : Table for Reinitialization
Partial & Custom meters Reset
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40704 | 9F00 | 1 | Input 1 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40705 | 9F01 | 1 | Input 2 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40706 | 9F02 | 1 | Input 3 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40707 | 9F03 | 1 | Input 4 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40708 | 9F04 | 1 | Input 5 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40709 | 9F05 | 1 | Input 6 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40710 | 9F06 | 1 | Input 7 Partial/Custom meters initialization 1 : Partial meter reset 2 : Custom meter reset 3 : Partial & Custom meter reset | Enumeration | 6, 16
| 40704 | 9F00 | 7
Input 1 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40711 | 9F07 | 2 | Protection code Total=0x010001;Partial=0x010002; Custom=0x010003;Reset=0x010004;All=0x010005 | / | 6, 16
| 40713 | 9F09 | 4 | Total meter value | Imp. (signed) | 6, 16
| 40717 | 9F0D | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40721 | 9F11 | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40723 | 9F13 | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40711 | 9F07 | 13
Input 2 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40724 | 9F14 | 2 | Protection code Total=0x020001;Partial=0x020002; Custom=0x020003;Reset=0x020004;All=0x020005 | / | 6, 16
| 40726 | 9F16 | 4 | Total meter value | Imp. (signed) | 6, 16
| 40730 | 9F1A | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40734 | 9F1E | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40736 | 9F20 | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40724 | 9F14 | 13
Input 3 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40737 | 9F21 | 2 | Protection code Total=0x040001;Partial=0x040002; Custom=0x040003;Reset=0x040004;All=0x040005 | / | 6, 16
| 40739 | 9F23 | 4 | Total meter value | Imp. (signed) | 6, 16
| 40743 | 9F27 | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40747 | 9F2B | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40749 | 9F2D | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40737 | 9F21 | 13
Input 4 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40750 | 9F2E | 2 | Protection code Total=0x080001;Partial=0x080002; Custom=0x080003;Reset=0x080004;All=0x080005 | / | 6, 16
| 40752 | 9F30 | 4 | Total meter value | Imp. (signed) | 6, 16
| 40756 | 9F34 | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40760 | 9F38 | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40762 | 9F3A | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40750 | 9F2E | 13
Input 5 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40763 | 9F3B | 2 | Protection code Total=0x100001;Partial=0x100002; Custom=0x100003;Reset=0x100004;All=0x100005 | / | 6, 16
| 40765 | 9F3D | 4 | Total meter value | Imp. (signed) | 6, 16
| 40769 | 9F41 | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40773 | 9F45 | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40775 | 9F47 | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40763 | 9F3B | 13
Input 6 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40776 | 9F48 | 2 | Protection code Total=0x020001;Partial=0x020002; Custom=0x020003;Reset=0x020004;All=0x020005 | / | 6, 16
| 40778 | 9F4A | 4 | Total meter value | Imp. (signed) | 6, 16
| 40782 | 9F4E | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40786 | 9F52 | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40788 | 9F54 | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40776 | 9F48 | 13
Input 7 meters initialization
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40789 | 9F55 | 2 | Protection code Total=0x040001;Partial=0x040002; Custom=0x040003;Reset=0x040004;All=0x040005 | / | 6, 16
| 40791 | 9F57 | 4 | Total meter value | Imp. (signed) | 6, 16
| 40795 | 9F5B | 4 | Partial meter value | Imp. (signed) | 6, 16
| 40799 | 9F5F | 2 | Custom meter value | Imp. (signed) | 6, 16
| 40801 | 9F61 | 1 | Reset 1 : Reset periodic meter 2 : Reset load curves | Enumeration | 6, 16
| 40789 | 9F55 | 13
98
A000 Hex : Table Detailed events
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 40960 | A000 | 1 | R1 Area |  | 6
| 40976 | A010 | 119 | R2 Area |  | 3
| 41095 | A087
R2 area : Data Area
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
Header | 40976 | A010 | 1 | Record count ( Maximum 9 ) |  | 3
| 40977 | A011 | 1 | Record size = 13 see below the data record description | Nb Words | 3
Data Buffer | 40978 | A012 | 117 | Records (x9) see below the description |  | 3
| 41095 | A087 | 119
Data record description
|  |  | Word Count | Description | Unit
|  |  | 1 | ID
|  |  | 1 | Type 0 : State 1 : Edge 2 : System | Enumeration
|  |  | 1 | Severity 0 : None 1 : Info 2 : Warning 3 : Default 4 : Error | Enumeration
|  |  | 1 | Status 0 : NonActive 1 : Active 2 : Finished 3 : Active and checked 4 : Finished and checked | Enumeration
|  |  | 2 | Date | Seconds since Jan 1, 2000
|  |  | 2 | Duration | Seconds
|  |  | 1 | Cause (depends of ID) | Enumeration
|  |  | 2 | Value low | signed
|  |  | 2 | Value high | signed
13

## Application Notes
APPLICATION NOTES
Historical data principle
The historical data can be read in two steps :
1 : Set the read pointer ( Write in the R1 register )
2 : Read the data buffer ( Read from the R2 register )
Command Area : Register R1 : Size 1 word
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| R1 ( DEC) | R1 ( Hex) | 1 | Actions : 0x0001 : Reset reader pointer : locate the pointer on the most recent value stored 0xFFFE : Get Next data packet ( pointer is updated ) |  | W
| R1 | R1 | 1
When the register R1 is writing with the value 1 : automaticaly the data buffer ( Regsiter R2 ) is filled with the most recent value stored
After this operation, to read the next data Write 0XFFFE in the register R1
Data Area : Register R2 = R1 +10Hex : ( size 125 Words )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
Header | R2(DEC) | R2(HEX) | 1 | Record count |  | R
| R2 +1 | R2 +1 | 1 | Record size : Y |  | R
| R2 +2 | R2 +2 | x | Data Header : this header may not exist according the historical type |  | R
Data Buffer | R3=R2 + 2 + x | R3=R2 + 2 + x | Y | Data |  | R
| R3 + Y | R3 + Y | Y | Data |  | R
| … | … | Y | Data |  | R
| …. | … | Y | Data |  | R
| R3+ n * Y | R3+ n * Y | Y | Data |  | R
The data area start always by two words :
1 : Record count : number of record present in the buffer
2 : Record Size : size of one data
Always read the complete area : function 16 with 125 Words
EN50160 Classification values
Sag classification
Duration t [ms]
Residual voltage u [%] | 20 < t < 200 | 200 < t < 500 | 500 < t < 1000 | 1000 < t < 5000 | 5000 < t <60000
90 > u >= 80 | 1 | 2 | 3 | 4 | 5
80 > u >= 70 | 6 | 7 | 8 | 9 | 10
70 > u >= 40 | 11 | 12 | 13 | 14 | 15
40 > u >= 5 | 16 | 17 | 18 | 19 | 20
5 > u | 21 | 22 | 23 | 24 | 25
Swell classification
Duration t [ms]
Swell voltage u [%] | 20 < t < 500 | 500 < t < 5000 | 5000 < t < 60000
u >= 120 | 26 | 27 | 28
120 > u >= 110 | 29 | 30 | 31