## Generalities
GENERALITIES
Generalities
The JBUS/MODBUS used by the product involves a dialogue using a master-slave hierarchical structure.
There are two possible dialogues :
- The master communicates with a slave and waits for its reply
- The master communicates with all the slaves without waiting for the reply
Hager products implement functions :
- 3 : to read n Words ( Maximum 125 words )
- 6 : to write 1 word
- 16 : to write n Word
The register type used are :
|  | long | 2 Words ( 4 bytes )
|  | int | 1 Word ( 2 Words )
If the register value is not available, according to its type and its signed, the indicated value is :
|  | unsigned long |  | FFFF FFFFhex
|  | signed long |  | 7FFF FFFF hex
|  | unsigned Int |  | FFFF hex
|  | signed int |  | 7FFF hex
Function 3 : Read n Words
Function 3 : Request frame format
Function 3 : Answer frame format
Number of Word asked in the Request frame
Data format is High and low order
Function 6 :Write 1 Word
Function 6 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network ( No answer is sent by the device )
Function 6 : Answer frame format
Function 16 :Write n Words
Function 16 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network : No answer is sent by the device
Function 16 : Answer frame format

## Product Tables
Product name : SM101C
C550 Hex : Metrology Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 50512 | C550 | 2 | Hour Meter | 1/100 h | 3 | 0xFFFFFFFF
| 50514 | C552 | 2 | Phase to Phase Voltage: U12 | V/100 | 3 | 0xFFFFFFFF
| 50516 | C554 | 2 | Phase to Phase Voltage: U23 | V/100 | 3 | 0xFFFFFFFF
| 50518 | C556 | 2 | Phase to Phase Voltage: U31 | V/100 | 3 | 0xFFFFFFFF
| 50520 | C558 | 2 | Simple voltage : V1 | V/100 | 3 | 0xFFFFFFFF
| 50522 | C55A | 2 | Simple voltage : V2 | V/100 | 3 | 0xFFFFFFFF
| 50524 | C55C | 2 | Simple voltage : V3 | V/100 | 3 | 0xFFFFFFFF
| 50526 | C55E | 2 | Frequency : F | Hz/100 | 3 | 0xFFFFFFFF
| 50528 | C560 | 2 | Current : I1 | mA | 3 | 0xFFFFFFFF
| 50530 | C562 | 2 | Current : I2 | mA | 3 | 0xFFFFFFFF
| 50532 | C564 | 2 | Current : I3 | mA | 3 | 0xFFFFFFFF
| 50534 | C566 | 2 | Neutral Current : In | mA | 3 | 0xFFFFFFFF
| 50536 | C568 | 2 | ∑ Active Power +/- : P | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50538 | C56A | 2 | ∑ Reactive Power +/- : Q | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50540 | C56C | 2 | ∑ Apparent Power : S | kVA/100 | 3 | 0xFFFFFFFF
| 50542 | C56E | 2 | ∑ Power Factor : -: leading et + : lagging : PF | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50544 | C570 | 2 | Active Power phase 1 +/- : P1 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50546 | C572 | 2 | Active Power phase 2 +/- : P2 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50548 | C574 | 2 | Active Power phase 3 +/- : P3 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50550 | C576 | 2 | Reactive Power phase 1 +/- : Q1 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50552 | C578 | 2 | Reactive Power phase 2 +/- : Q2 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50554 | C57A | 2 | Reactive Power phase 3 +/- : Q3 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50556 | C57C | 2 | Apparent Power phase 1 : S1 | kVA/100 | 3 | 0xFFFFFFFF
| 50558 | C57E | 2 | Apparent Power phase 2 : S2 | kVA/100 | 3 | 0xFFFFFFFF
| 50560 | C580 | 2 | Apparent Power phase 3 : S3 | kVA/100 | 3 | 0xFFFFFFFF
| 50562 | C582 | 2 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50564 | C584 | 2 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50566 | C586 | 2 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0,001 (Signed) | 3 | 0x7FFFFFFF
Not applicable | 50568 | C588 | 2 | System value I Sys = ( I1+I2+I3) / 3 | mA | 3 | 0xFFFFFFFF
Not applicable | 50570 | C58A | 2 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 50572 | C58C | 2 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | 3 | 0xFFFFFFFF
| 50512 | C550 | 62
C650 Hex : Energies
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 50768 | C650 | 2 | Hour meter | 1/100 h | 3 | 0xFFFFFFFF
Not applicable | 50770 | C652 | 2 | Total Positive Active Energy (no resetable) : Ea+ | kWh | 3 | 0xFFFFFFFF
Not applicable | 50772 | C654 | 2 | Total Positive Reactive Energy (no resetable) : Er + | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50774 | C656 | 2 | Total Apparent Energy (no resetable) : Es | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50776 | C658 | 2 | Total Negative Active Energy (no resetable) : Ea- | kWh | 3 | 0xFFFFFFFF
Not applicable | 50778 | C65A | 2 | Total Negative Reactive Energy (no resetable) : Er - | kvarh | 3 | 0xFFFFFFFF
| 50780 | C65C | 2 | Partial Positive Active Energy: Ea+ | kWh | 3 | 0xFFFFFFFF
| 50782 | C65E | 2 | Partial Positive Reactive Energy: Er + | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50784 | C660 | 2 | Partial Apparent Energy : Es | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50786 | C662 | 2 | Partial Negative Active Energy : Ea- | kWh | 3 | 0xFFFFFFFF
Not applicable | 50788 | C664 | 2 | Partial Negative Reactive Energy : Er - | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50790 | C666 | 2 | Number of pulse meter to read (from 0 to 10 max) | - | 3 | 0xFFFFFFFF
Not applicable | 50792 | C668 | 2 | Total pulse meter Input 1 | - | 3 | 0xFFFFFFFF
Not applicable | 50794 | C66A | 2 | Total pulse meter Input 2 | - | 3 | 0xFFFFFFFF
Not applicable | 50796 | C66C | 2 | Total pulse meter Input 3 | - | 3 | 0xFFFFFFFF
Not applicable | 50798 | C66E | 2 | Total pulse meter Input 4 | - | 3 | 0xFFFFFFFF
Not applicable | 50800 | C670 | 2 | Total pulse meter Input 5 | - | 3 | 0xFFFFFFFF
Not applicable | 50802 | C672 | 2 | Total pulse meter Input 6 | - | 3 | 0xFFFFFFFF
Not applicable | 50804 | C674 | 2 | Total pulse meter Input 7 | - | 3 | 0xFFFFFFFF
Not applicable | 50806 | C676 | 2 | Total pulse meter Input 8 | - | 3 | 0xFFFFFFFF
Not applicable | 50808 | C678 | 2 | Total pulse meter Input 9 | - | 3 | 0xFFFFFFFF
Not applicable | 50810 | C67A | 2 | Total pulse meter Input 10 | - | 3 | 0xFFFFFFFF
Not applicable | 50812 | C67C | 2 | Predictive Active Power | kWh | 3 | 0xFFFFFFFF
Not applicable | 50814 | C67E | 2 | Predictive Reactive Power | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50816 | C680 | 2 | Predictive Apparent Power | kVAh | 3 | 0xFFFFFFFF
Not applicable | 50818 | C682 | 2 | Mean positive active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
Not applicable | 50820 | C684 | 2 | Mean negative active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
Not applicable | 50822 | C686 | 2 | Mean positive reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
Not applicable | 50824 | C688 | 2 | Mean negative reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
Not applicable | 50826 | C68A | 2 | Last date for Record average P/Q/S in second since 01/01/2000 | s | 3 | 0xFFFFFFFF
Not applicable | 50828 | C68C | 1 | Last average (P+) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50829 | C68D | 1 | Last average (Q+) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50830 | C68E | 1 | Last average (P-) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50831 | C68F | 1 | Last average (Q-) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
Not applicable | 50832 | C690 | 1 | Last average S | VA ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50768 | C650 | 65
C750 Hex : Statistique Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
Not applicable | 51024 | C750 | 2 | Avg U12 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51026 | C752 | 2 | Avg U23 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51028 | C754 | 2 | Avg U31 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51030 | C756 | 2 | Avg V1 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51032 | C758 | 2 | Avg V2 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51034 | C75A | 2 | Avg V3 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51036 | C75C | 2 | Avg F | Hz/100 | 3 | 0xFFFFFFFF
Not applicable | 51038 | C75E | 2 | Avg I1 | mA | 3 | 0xFFFFFFFF
Not applicable | 51040 | C760 | 2 | Avg I2 | mA | 3 | 0xFFFFFFFF
Not applicable | 51042 | C762 | 2 | Avg I3 | mA | 3 | 0xFFFFFFFF
Not applicable | 51044 | C764 | 2 | Avg In | mA | 3 | 0xFFFFFFFF
Not applicable | 51046 | C766 | 2 | Avg P+ (∑ active power +) | kW/100 | 3 | 0xFFFFFFFF
Not applicable | 51048 | C768 | 2 | Avg P- (∑ active power -) | kW/100 | 3 | 0xFFFFFFFF
Not applicable | 51050 | C76A | 2 | Avg Q+ (∑ reactive power +) | kvar/100 | 3 | 0xFFFFFFFF
Not applicable | 51052 | C76C | 2 | Avg Q-(∑ reactive power -) | kvar/100 | 3 | 0xFFFFFFFF
Not applicable | 51054 | C76E | 2 | Avg S (∑ apparent power) | kVA/100 | 3 | 0xFFFFFFFF
Not applicable | 51056 | C770 | 2 | Max/avg U12 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51058 | C772 | 2 | Max/avg U23 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51060 | C774 | 2 | Max/avg U31 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51062 | C776 | 2 | Max/avg V1 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51064 | C778 | 2 | Max/avg V2 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51066 | C77A | 2 | Max/avg V3 | V/100 | 3 | 0xFFFFFFFF
Not applicable | 51068 | C77C | 2 | Max/avg F | Hz/100 | 3 | 0xFFFFFFFF
| 51070 | C77E | 2 | Max/avg I1 | mA | 3 | 0xFFFFFFFF
| 51072 | C780 | 2 | Max/avg I2 | mA | 3 | 0xFFFFFFFF
| 51074 | C782 | 2 | Max/avg I3 | mA | 3 | 0xFFFFFFFF
| 51076 | C784 | 2 | Max/avg In | mA | 3 | 0xFFFFFFFF
| 51078 | C786 | 2 | Max/avg P+ | kW/100 | 3 | 0xFFFFFFFF
| 51080 | C788 | 2 | Max/avg P- | kW/100 | 3 | 0xFFFFFFFF
| 51082 | C78A | 2 | Max/avg Q+ | kvar/100 | 3 | 0xFFFFFFFF
| 51084 | C78C | 2 | Max/avg Q- | kvar/100 | 3 | 0xFFFFFFFF
| 51086 | C78E | 2 | Max/avg S | kVA/100 | 3 | 0xFFFFFFFF
Not applicable | 51088 | C790 | 1 | Minimum THD I | 0.1% | 3 | 0xFFFF
Not applicable | 51089 | C791 | 1 | Minimum THD In | 0.1% | 3 | 0xFFFF
Not applicable | 51090 | C792 | 1 | Minimum THD U | 0.1% | 3 | 0xFFFF
Not applicable | 51091 | C793 | 1 | Maximum THD I | 0.1% | 3 | 0xFFFF
Not applicable | 51092 | C794 | 1 | Maximum THD In | 0.1% | 3 | 0xFFFF
Not applicable | 51093 | C795 | 1 | Maximum THD U | 0.1% | 3 | 0xFFFF
| 51024 | C750 | 70
C850 Hex : Metrology No Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 51280 | C850 | 1 | Hour Meter | h | 3 | 0xFFFF
| 51281 | C851 | 1 | Phase to Phase Voltage: U12 | V/100 | 3 | 0xFFFF
| 51282 | C852 | 1 | Phase to Phase Voltage: U23 | V/100 | 3 | 0xFFFF
| 51283 | C853 | 1 | Phase to Phase Voltage: U31 | V/100 | 3 | 0xFFFF
| 51284 | C854 | 1 | Simple voltage : V1 | V/100 | 3 | 0xFFFF
| 51285 | C855 | 1 | Simple voltage : V2 | V/100 | 3 | 0xFFFF
| 51286 | C856 | 1 | Simple voltage : V3 | V/100 | 3 | 0xFFFF
| 51287 | C857 | 1 | Frequency : F | Hz/100 | 3 | 0xFFFF
| 51288 | C858 | 1 | Current : I1 | mA | 3 | 0xFFFF
| 51289 | C859 | 1 | Current : I2 | mA | 3 | 0xFFFF
| 51290 | C85A | 1 | Current : I3 | mA | 3 | 0xFFFF
| 51291 | C85B | 1 | Neutral Current : In | mA | 3 | 0xFFFF
| 51292 | C85C | 1 | ∑ active Power +/- : P | kW/100 (Signed) | 3 | 0x7FFF
| 51293 | C85D | 1 | ∑ aeactive Power +/- : Q | kvar/100 (Signed) | 3 | 0x7FFF
| 51294 | C85E | 1 | ∑ apparent power : S | kVA/100 | 3 | 0xFFFF
| 51295 | C85F | 1 | ∑ power factor : -: leading and + : lagging : PF | 0,001 (Signed) | 3 | 0x7FFF
| 51296 | C860 | 1 | Active Power phase 1 +/- : P1 | kW/100 (Signed) | 3 | 0x7FFF
| 51297 | C861 | 1 | Active Power phase 2 +/- : P2 | kW/100 (Signed) | 3 | 0x7FFF
| 51298 | C862 | 1 | Active Power phase 3 +/- : P3 | kW/100 (Signed) | 3 | 0x7FFF
| 51299 | C863 | 1 | Reactive Power phase 1 +/- : Q1 | kvar/100 (Signed) | 3 | 0x7FFF
| 51300 | C864 | 1 | Reactive Power phase 2 +/- : Q2 | kvar/100 (Signed) | 3 | 0x7FFF
| 51301 | C865 | 1 | Reactive Power phase 3 +/- : Q3 | kvar/100 (Signed) | 3 | 0x7FFF
| 51302 | C866 | 1 | Apparent power phase 1 : S1 | kVA/100 | 3 | 0xFFFF
| 51303 | C867 | 1 | Apparent power phase 2 : S2 | kVA/100 | 3 | 0xFFFF
| 51304 | C868 | 1 | Apparent power phase 3 : S3 | kVA/100 | 3 | 0xFFFF
| 51305 | C869 | 1 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0,001 (Signed) | 3 | 0x7FFF
| 51306 | C86A | 1 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0,001 (Signed) | 3 | 0x7FFF
| 51307 | C86B | 1 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0,001 (Signed) | 3 | 0x7FFF
Not applicable | 51308 | C86C | 1 | System value I Sys = ( I1+I2+I3) / 3 | mA | 3 | 0xFFFF
Not applicable | 51309 | C86D | 1 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | 3 | 0xFFFF
Not applicable | 51310 | C86E | 1 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | 3 | 0xFFFF
| 51311 | C86F | 1 | Total Positive Active Energy (no resetable) : Ea+ | MWh | 3 | 0xFFFF
Not applicable | 51312 | C870 | 1 | Total Positive Reactive Energy (no resetable) : Er + | Mvarh | 3 | 0xFFFF
| 51313 | C871 | 1 | Total Negative Active Energy (no resetable) : Ea- | MWh | 3 | 0xFFFF
Not applicable | 51314 | C872 | 1 | Total Negative Reactive Energy (no resetable) : Er - | Mvarh | 3 | 0xFFFF
| 51280 | C850 | 35
C900 Hex : Temperatures
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 51456 | C900 | 1 | Internal module Temperature present | yes(1) / no (0) | 3
| 51457 | C901 | 1 | module Temperature | celsius degre | 3
Not applicable | 51458 | C902 | 1 | Number of external Temperature sensors to read (from 0 to 5 max) | - | 3
Not applicable | 51459 | C903 | 1 | Temperature extern 1 | celsius degre | 3
Not applicable | 51460 | C904 | 1 | Temperature extern 2 | celsius degre | 3
Not applicable | 51461 | C905 | 1 | Temperature extern 3 | celsius degre | 3
Not applicable | 51462 | C906 | 1 | Temperature extern 4 | celsius degre | 3
Not applicable | 51463 | C907 | 1 | Temperature extern 5 | celsius degre | 3
| 51456 | C900 | 8
C6A0 Hex : Energies per tariff
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 50848 | C6A0 | 1 | 0 >= Tariff number <= 8 |  | 3 | 0
| 50849 | C6A1 | 1 | Tariff number in progress ( 1 to 8 ) |  | 3 | 0
| 50850 | C6A2 | 16 | 8 * Positive Active Energies | kWh | 3 | 0xFFFFFFFF
| 50866 | C6B2 | 16 | 8 * Positive Reactive Enegies | kvarh | 3 | 0xFFFFFFFF
Not applicable | 50882 | C6C2 | 16 | 8 * Time Counter | 1/100 h | 3 | 0xFFFFFFFF
| 50848 | C6A0 | 50
C950 Hex : Harmonic
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
THD
| 51536 | C950 | 1 | thd U12 | 0.1% | 3 | 0XFFFF
| 51537 | C951 | 1 | thd U23 | 0.1% | 3 | 0XFFFF
| 51538 | C952 | 1 | thd U31 | 0.1% | 3 | 0XFFFF
| 51539 | C953 | 1 | thd V1 | 0.1% | 3 | 0XFFFF
| 51540 | C954 | 1 | thd V2 | 0.1% | 3 | 0XFFFF
| 51541 | C955 | 1 | thd V3 | 0.1% | 3 | 0XFFFF
| 51542 | C956 | 1 | thd I1 | 0.1% | 3 | 0XFFFF
| 51543 | C957 | 1 | thd I2 | 0.1% | 3 | 0XFFFF
| 51544 | C958 | 1 | thd I3 | 0.1% | 3 | 0XFFFF
| 51545 | C959 | 1 | thd In | 0.1% | 3 | 0XFFFF
| 51536 | C950 | 10
I : harmonic order
Not applicable | 51546 | C95A | 1 | Number of harmonic rows |  | 3 | 0
Not applicable | 51547 | C95B | 1 | harmonic I1 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51548 | C95C | 1 | harmonic I2 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51549 | C95D | 1 | harmonic I3 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51550 | C95E | 1 | harmonic IN row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51551 | C95F | 1 | harmonic I1 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51552 | C960 | 1 | harmonic I2 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51553 | C961 | 1 | harmonic I3 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51554 | C962 | 1 | harmonic IN row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51555 | C963 | 1 | harmonic I1 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51556 | C964 | 1 | harmonic I2 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51557 | C965 | 1 | harmonic I3 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51558 | C966 | 1 | harmonic IN row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51559 | C967 | 1 | harmonic I1 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51560 | C968 | 1 | harmonic I2 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51561 | C969 | 1 | harmonic I3 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51562 | C96A | 1 | harmonic IN row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51563 | C96B | 1 | harmonic I1 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51564 | C96C | 1 | harmonic I2 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51565 | C96D | 1 | harmonic I3 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51566 | C96E | 1 | harmonic IN row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51567 | C96F | 1 | harmonic I1 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51568 | C970 | 1 | harmonic I2 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51569 | C971 | 1 | harmonic I3 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51570 | C972 | 1 | harmonic IN row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51571 | C973 | 1 | harmonic I1 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51572 | C974 | 1 | harmonic I2 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51573 | C975 | 1 | harmonic I3 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51574 | C976 | 1 | harmonic IN row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51575 | C977 | 1 | harmonic I1 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51576 | C978 | 1 | harmonic I2 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51577 | C979 | 1 | harmonic I3 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51578 | C97A | 1 | harmonic IN row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51579 | C97B | 1 | harmonic I1 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51580 | C97C | 1 | harmonic I2 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51581 | C97D | 1 | harmonic I3 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51582 | C97E | 1 | harmonic IN row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51583 | C97F | 1 | harmonic I1 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51584 | C980 | 1 | harmonic I2 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51585 | C981 | 1 | harmonic I3 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51586 | C982 | 1 | harmonic IN row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51587 | C983 | 1 | harmonic I1 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51588 | C984 | 1 | harmonic I2 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51589 | C985 | 1 | harmonic I3 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51590 | C986 | 1 | harmonic IN row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51591 | C987 | 1 | harmonic I1 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51592 | C988 | 1 | harmonic I2 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51593 | C989 | 1 | harmonic I3 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51594 | C98A | 1 | harmonic IN row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51595 | C98B | 1 | harmonic I1 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51596 | C98C | 1 | harmonic I2 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51597 | C98D | 1 | harmonic I3 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51598 | C98E | 1 | harmonic IN row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51599 | C98F | 1 | harmonic I1 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51600 | C990 | 1 | harmonic I2 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51601 | C991 | 1 | harmonic I3 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51602 | C992 | 1 | harmonic IN row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51603 | C993 | 1 | harmonic I1 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51604 | C994 | 1 | harmonic I2 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51605 | C995 | 1 | harmonic I3 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51606 | C996 | 1 | harmonic IN row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51607 | C997 | 1 | harmonic I1 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51608 | C998 | 1 | harmonic I2 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51609 | C999 | 1 | harmonic I3 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51610 | C99A | 1 | harmonic IN row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51611 | C99B | 1 | harmonic I1 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51612 | C99C | 1 | harmonic I2 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51613 | C99D | 1 | harmonic I3 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51614 | C99E | 1 | harmonic IN row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51615 | C99F | 1 | harmonic I1 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51616 | C9A0 | 1 | harmonic I2 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51617 | C9A1 | 1 | harmonic I3 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51618 | C9A2 | 1 | harmonic IN row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51619 | C9A3 | 1 | harmonic I1 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51620 | C9A4 | 1 | harmonic I2 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51621 | C9A5 | 1 | harmonic I3 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51622 | C9A6 | 1 | harmonic IN row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51623 | C9A7 | 1 | harmonic I1 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51624 | C9A8 | 1 | harmonic I2 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51625 | C9A9 | 1 | harmonic I3 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51626 | C9AA | 1 | harmonic IN row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51627 | C9AB | 1 | harmonic I1 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51628 | C9AC | 1 | harmonic I2 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51629 | C9AD | 1 | harmonic I3 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51630 | C9AE | 1 | harmonic IN row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51631 | C9AF | 1 | harmonic I1 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51632 | C9B0 | 1 | harmonic I2 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51633 | C9B1 | 1 | harmonic I3 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51634 | C9B2 | 1 | harmonic IN row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51635 | C9B3 | 1 | harmonic I1 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51636 | C9B4 | 1 | harmonic I2 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51637 | C9B5 | 1 | harmonic I3 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51638 | C9B6 | 1 | harmonic IN row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51639 | C9B7 | 1 | harmonic I1 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51640 | C9B8 | 1 | harmonic I2 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51641 | C9B9 | 1 | harmonic I3 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51642 | C9BA | 1 | harmonic IN row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51643 | C9BB | 1 | harmonic I1 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51644 | C9BC | 1 | harmonic I2 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51645 | C9BD | 1 | harmonic I3 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51646 | C9BE | 1 | harmonic IN row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51647 | C9BF | 1 | harmonic I1 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51648 | C9C0 | 1 | harmonic I2 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51649 | C9C1 | 1 | harmonic I3 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51650 | C9C2 | 1 | harmonic IN row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51651 | C9C3 | 1 | harmonic I1 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51652 | C9C4 | 1 | harmonic I2 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51653 | C9C5 | 1 | harmonic I3 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51654 | C9C6 | 1 | harmonic IN row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51655 | C9C7 | 1 | harmonic I1 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51656 | C9C8 | 1 | harmonic I2 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51657 | C9C9 | 1 | harmonic I3 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51658 | C9CA | 1 | harmonic IN row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51659 | C9CB | 1 | harmonic I1 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51660 | C9CC | 1 | harmonic I2 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51661 | C9CD | 1 | harmonic I3 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51662 | C9CE | 1 | harmonic IN row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51663 | C9CF | 1 | harmonic I1 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51664 | C9D0 | 1 | harmonic I2 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51665 | C9D1 | 1 | harmonic I3 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51666 | C9D2 | 1 | harmonic IN row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51667 | C9D3 | 1 | harmonic I1 row 63 | 0.1% | 3 | 0XFFFF
Not applicable | 51668 | C9D4 | 1 | harmonic I2 row 63 | 0.1% | 3 | 0XFFFF
Not applicable | 51669 | C9D5 | 1 | harmonic I3 row 63 | 0.1% | 3 | 0XFFFF
Not applicable | 51670 | C9D6 | 1 | harmonic IN row 63 | 0.1% | 3 | 0XFFFF
| 51546 | C95A | 125
V PH/Ph :harmonic order
Not applicable | 51671 | C9D7 | 1 | Number of harmonic rows |  | 3 | 0
Not applicable | 51672 | C9D8 | 1 | harmonic U12 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51673 | C9D9 | 1 | harmonic U23 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51674 | C9DA | 1 | harmonic U31 row 3 | 0.1% | 3 | 0XFFFF
Not applicable | 51675 | C9DB | 1 | harmonic U12 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51676 | C9DC | 1 | harmonic U23 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51677 | C9DD | 1 | harmonic U31 row 5 | 0.1% | 3 | 0XFFFF
Not applicable | 51678 | C9DE | 1 | harmonic U12 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51679 | C9DF | 1 | harmonic U23 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51680 | C9E0 | 1 | harmonic U31 row 7 | 0.1% | 3 | 0XFFFF
Not applicable | 51681 | C9E1 | 1 | harmonic U12 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51682 | C9E2 | 1 | harmonic U23 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51683 | C9E3 | 1 | harmonic U31 row 9 | 0.1% | 3 | 0XFFFF
Not applicable | 51684 | C9E4 | 1 | harmonic U12 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51685 | C9E5 | 1 | harmonic U23 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51686 | C9E6 | 1 | harmonic U31 row 11 | 0.1% | 3 | 0XFFFF
Not applicable | 51687 | C9E7 | 1 | harmonic U12 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51688 | C9E8 | 1 | harmonic U23 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51689 | C9E9 | 1 | harmonic U31 row 13 | 0.1% | 3 | 0XFFFF
Not applicable | 51690 | C9EA | 1 | harmonic U12 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51691 | C9EB | 1 | harmonic U23 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51692 | C9EC | 1 | harmonic U31 row 15 | 0.1% | 3 | 0XFFFF
Not applicable | 51693 | C9ED | 1 | harmonic U12 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51694 | C9EE | 1 | harmonic U23 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51695 | C9EF | 1 | harmonic U31 row 17 | 0.1% | 3 | 0XFFFF
Not applicable | 51696 | C9F0 | 1 | harmonic U12 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51697 | C9F1 | 1 | harmonic U23 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51698 | C9F2 | 1 | harmonic U31 row 19 | 0.1% | 3 | 0XFFFF
Not applicable | 51699 | C9F3 | 1 | harmonic U12 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51700 | C9F4 | 1 | harmonic U23 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51701 | C9F5 | 1 | harmonic U31 row 21 | 0.1% | 3 | 0XFFFF
Not applicable | 51702 | C9F6 | 1 | harmonic U12 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51703 | C9F7 | 1 | harmonic U23 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51704 | C9F8 | 1 | harmonic U31 row 23 | 0.1% | 3 | 0XFFFF
Not applicable | 51705 | C9F9 | 1 | harmonic U12 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51706 | C9FA | 1 | harmonic U23 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51707 | C9FB | 1 | harmonic U31 row 25 | 0.1% | 3 | 0XFFFF
Not applicable | 51708 | C9FC | 1 | harmonic U12 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51709 | C9FD | 1 | harmonic U23 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51710 | C9FE | 1 | harmonic U31 row 27 | 0.1% | 3 | 0XFFFF
Not applicable | 51711 | C9FF | 1 | harmonic U12 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51712 | CA00 | 1 | harmonic U23 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51713 | CA01 | 1 | harmonic U31 row 29 | 0.1% | 3 | 0XFFFF
Not applicable | 51714 | CA02 | 1 | harmonic U12 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51715 | CA03 | 1 | harmonic U23 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51716 | CA04 | 1 | harmonic U31 row 31 | 0.1% | 3 | 0XFFFF
Not applicable | 51717 | CA05 | 1 | harmonic U12 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51718 | CA06 | 1 | harmonic U23 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51719 | CA07 | 1 | harmonic U31 row 33 | 0.1% | 3 | 0XFFFF
Not applicable | 51720 | CA08 | 1 | harmonic U12 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51721 | CA09 | 1 | harmonic U23 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51722 | CA0A | 1 | harmonic U31 row 35 | 0.1% | 3 | 0XFFFF
Not applicable | 51723 | CA0B | 1 | harmonic U12 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51724 | CA0C | 1 | harmonic U23 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51725 | CA0D | 1 | harmonic U31 row 37 | 0.1% | 3 | 0XFFFF
Not applicable | 51726 | CA0E | 1 | harmonic U12 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51727 | CA0F | 1 | harmonic U23 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51728 | CA10 | 1 | harmonic U31 row 39 | 0.1% | 3 | 0XFFFF
Not applicable | 51729 | CA11 | 1 | harmonic U12 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51730 | CA12 | 1 | harmonic U23 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51731 | CA13 | 1 | harmonic U31 row 41 | 0.1% | 3 | 0XFFFF
Not applicable | 51732 | CA14 | 1 | harmonic U12 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51733 | CA15 | 1 | harmonic U23 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51734 | CA16 | 1 | harmonic U31 row 43 | 0.1% | 3 | 0XFFFF
Not applicable | 51735 | CA17 | 1 | harmonic U12 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51736 | CA18 | 1 | harmonic U23 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51737 | CA19 | 1 | harmonic U31 row 45 | 0.1% | 3 | 0XFFFF
Not applicable | 51738 | CA1A | 1 | harmonic U12 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51739 | CA1B | 1 | harmonic U23 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51740 | CA1C | 1 | harmonic U31 row 47 | 0.1% | 3 | 0XFFFF
Not applicable | 51741 | CA1D | 1 | harmonic U12 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51742 | CA1E | 1 | harmonic U23 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51743 | CA1F | 1 | harmonic U31 row 49 | 0.1% | 3 | 0XFFFF
Not applicable | 51744 | CA20 | 1 | harmonic U12 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51745 | CA21 | 1 | harmonic U23 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51746 | CA22 | 1 | harmonic U31 row 51 | 0.1% | 3 | 0XFFFF
Not applicable | 51747 | CA23 | 1 | harmonic U12 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51748 | CA24 | 1 | harmonic U23 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51749 | CA25 | 1 | harmonic U31 row 53 | 0.1% | 3 | 0XFFFF
Not applicable | 51750 | CA26 | 1 | harmonic U12 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51751 | CA27 | 1 | harmonic U23 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51752 | CA28 | 1 | harmonic U31 row 55 | 0.1% | 3 | 0XFFFF
Not applicable | 51753 | CA29 | 1 | harmonic U12 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51754 | CA2A | 1 | harmonic U23 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51755 | CA2B | 1 | harmonic U31 row 57 | 0.1% | 3 | 0XFFFF
Not applicable | 51756 | CA2C | 1 | harmonic U12 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51757 | CA2D | 1 | harmonic U23 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51758 | CA2E | 1 | harmonic U31 row 59 | 0.1% | 3 | 0XFFFF
Not applicable | 51759 | CA2F | 1 | harmonic U12 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51760 | CA30 | 1 | harmonic U23 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51761 | CA31 | 1 | harmonic U31 row 61 | 0.1% | 3 | 0XFFFF
Not applicable | 51762 | CA32 | 1 | harmonic U12 row 63 | 0.1% | 3 | 0XFFFF
Not applicable | 51763 | CA33 | 1 | harmonic U23 row 63 | 0.1% | 3 | 0XFFFF
Not applicable | 51764 | CA34 | 1 | harmonic U31 row 63 | 0.1% | 3 | 0XFFFF
| 51671 | C9D7 | 94
V PH/N : harmonic order
Not applicable | 51765 | CA35 | 1 | Number of harmonic rows |  | 3 | 0
Not applicable | 51766 | CA36 | 1 | harmonic V1 row 3 | 0.1% | 3 | 0xFFFF
Not applicable | 51767 | CA37 | 1 | harmonic V2 row 3 | 0.1% | 3 | 0xFFFF
Not applicable | 51768 | CA38 | 1 | harmonic V3 row 3 | 0.1% | 3 | 0xFFFF
Not applicable | 51769 | CA39 | 1 | harmonic V1 row 5 | 0.1% | 3 | 0xFFFF
Not applicable | 51770 | CA3A | 1 | harmonic V2 row 5 | 0.1% | 3 | 0xFFFF
Not applicable | 51771 | CA3B | 1 | harmonic V3 row 5 | 0.1% | 3 | 0xFFFF
Not applicable | 51772 | CA3C | 1 | harmonic V1 row 7 | 0.1% | 3 | 0xFFFF
Not applicable | 51773 | CA3D | 1 | harmonic V2 row 7 | 0.1% | 3 | 0xFFFF
Not applicable | 51774 | CA3E | 1 | harmonic V3 row 7 | 0.1% | 3 | 0xFFFF
Not applicable | 51775 | CA3F | 1 | harmonic V1 row 9 | 0.1% | 3 | 0xFFFF
Not applicable | 51776 | CA40 | 1 | harmonic V2 row 9 | 0.1% | 3 | 0xFFFF
Not applicable | 51777 | CA41 | 1 | harmonic V3 row 9 | 0.1% | 3 | 0xFFFF
Not applicable | 51778 | CA42 | 1 | harmonic V1 row 11 | 0.1% | 3 | 0xFFFF
Not applicable | 51779 | CA43 | 1 | harmonic V2 row 11 | 0.1% | 3 | 0xFFFF
Not applicable | 51780 | CA44 | 1 | harmonic V3 row 11 | 0.1% | 3 | 0xFFFF
Not applicable | 51781 | CA45 | 1 | harmonic V1 row 13 | 0.1% | 3 | 0xFFFF
Not applicable | 51782 | CA46 | 1 | harmonic V2 row 13 | 0.1% | 3 | 0xFFFF
Not applicable | 51783 | CA47 | 1 | harmonic V3 row 13 | 0.1% | 3 | 0xFFFF
Not applicable | 51784 | CA48 | 1 | harmonic V1 row 15 | 0.1% | 3 | 0xFFFF
Not applicable | 51785 | CA49 | 1 | harmonic V2 row 15 | 0.1% | 3 | 0xFFFF
Not applicable | 51786 | CA4A | 1 | harmonic V3 row 15 | 0.1% | 3 | 0xFFFF
Not applicable | 51787 | CA4B | 1 | harmonic V1 row 17 | 0.1% | 3 | 0xFFFF
Not applicable | 51788 | CA4C | 1 | harmonic V2 row 17 | 0.1% | 3 | 0xFFFF
Not applicable | 51789 | CA4D | 1 | harmonic V3 row 17 | 0.1% | 3 | 0xFFFF
Not applicable | 51790 | CA4E | 1 | harmonic V1 row 19 | 0.1% | 3 | 0xFFFF
Not applicable | 51791 | CA4F | 1 | harmonic V2 row 19 | 0.1% | 3 | 0xFFFF
Not applicable | 51792 | CA50 | 1 | harmonic V3 row 19 | 0.1% | 3 | 0xFFFF
Not applicable | 51793 | CA51 | 1 | harmonic V1 row 21 | 0.1% | 3 | 0xFFFF
Not applicable | 51794 | CA52 | 1 | harmonic V2 row 21 | 0.1% | 3 | 0xFFFF
Not applicable | 51795 | CA53 | 1 | harmonic V3 row 21 | 0.1% | 3 | 0xFFFF
Not applicable | 51796 | CA54 | 1 | harmonic V1 row 23 | 0.1% | 3 | 0xFFFF
Not applicable | 51797 | CA55 | 1 | harmonic V2 row 23 | 0.1% | 3 | 0xFFFF
Not applicable | 51798 | CA56 | 1 | harmonic V3 row 23 | 0.1% | 3 | 0xFFFF
Not applicable | 51799 | CA57 | 1 | harmonic V1 row 25 | 0.1% | 3 | 0xFFFF
Not applicable | 51800 | CA58 | 1 | harmonic V2 row 25 | 0.1% | 3 | 0xFFFF
Not applicable | 51801 | CA59 | 1 | harmonic V3 row 25 | 0.1% | 3 | 0xFFFF
Not applicable | 51802 | CA5A | 1 | harmonic V1 row 27 | 0.1% | 3 | 0xFFFF
Not applicable | 51803 | CA5B | 1 | harmonic V2 row 27 | 0.1% | 3 | 0xFFFF
Not applicable | 51804 | CA5C | 1 | harmonic V3 row 27 | 0.1% | 3 | 0xFFFF
Not applicable | 51805 | CA5D | 1 | harmonic V1 row 29 | 0.1% | 3 | 0xFFFF
Not applicable | 51806 | CA5E | 1 | harmonic V2 row 29 | 0.1% | 3 | 0xFFFF
Not applicable | 51807 | CA5F | 1 | harmonic V3 row 29 | 0.1% | 3 | 0xFFFF
Not applicable | 51808 | CA60 | 1 | harmonic V1 row 31 | 0.1% | 3 | 0xFFFF
Not applicable | 51809 | CA61 | 1 | harmonic V2 row 31 | 0.1% | 3 | 0xFFFF
Not applicable | 51810 | CA62 | 1 | harmonic V3 row 31 | 0.1% | 3 | 0xFFFF
Not applicable | 51811 | CA63 | 1 | harmonic V1 row 33 | 0.1% | 3 | 0xFFFF
Not applicable | 51812 | CA64 | 1 | harmonic V2 row 33 | 0.1% | 3 | 0xFFFF
Not applicable | 51813 | CA65 | 1 | harmonic V3 row 33 | 0.1% | 3 | 0xFFFF
Not applicable | 51814 | CA66 | 1 | harmonic V1 row 35 | 0.1% | 3 | 0xFFFF
Not applicable | 51815 | CA67 | 1 | harmonic V2 row 35 | 0.1% | 3 | 0xFFFF
Not applicable | 51816 | CA68 | 1 | harmonic V3 row 35 | 0.1% | 3 | 0xFFFF
Not applicable | 51817 | CA69 | 1 | harmonic V1 row 37 | 0.1% | 3 | 0xFFFF
Not applicable | 51818 | CA6A | 1 | harmonic V2 row 37 | 0.1% | 3 | 0xFFFF
Not applicable | 51819 | CA6B | 1 | harmonic V3 row 37 | 0.1% | 3 | 0xFFFF
Not applicable | 51820 | CA6C | 1 | harmonic V1 row 39 | 0.1% | 3 | 0xFFFF
Not applicable | 51821 | CA6D | 1 | harmonic V2 row 39 | 0.1% | 3 | 0xFFFF
Not applicable | 51822 | CA6E | 1 | harmonic V3 row 39 | 0.1% | 3 | 0xFFFF
Not applicable | 51823 | CA6F | 1 | harmonic V1 row 41 | 0.1% | 3 | 0xFFFF
Not applicable | 51824 | CA70 | 1 | harmonic V2 row 41 | 0.1% | 3 | 0xFFFF
Not applicable | 51825 | CA71 | 1 | harmonic V3 row 41 | 0.1% | 3 | 0xFFFF
Not applicable | 51826 | CA72 | 1 | harmonic V1 row 43 | 0.1% | 3 | 0xFFFF
Not applicable | 51827 | CA73 | 1 | harmonic V2 row 43 | 0.1% | 3 | 0xFFFF
Not applicable | 51828 | CA74 | 1 | harmonic V3 row 43 | 0.1% | 3 | 0xFFFF
Not applicable | 51829 | CA75 | 1 | harmonic V1 row 45 | 0.1% | 3 | 0xFFFF
Not applicable | 51830 | CA76 | 1 | harmonic V2 row 45 | 0.1% | 3 | 0xFFFF
Not applicable | 51831 | CA77 | 1 | harmonic V3 row 45 | 0.1% | 3 | 0xFFFF
Not applicable | 51832 | CA78 | 1 | harmonic V1 row 47 | 0.1% | 3 | 0xFFFF
Not applicable | 51833 | CA79 | 1 | harmonic V2 row 47 | 0.1% | 3 | 0xFFFF
Not applicable | 51834 | CA7A | 1 | harmonic V3 row 47 | 0.1% | 3 | 0xFFFF
Not applicable | 51835 | CA7B | 1 | harmonic V1 row 49 | 0.1% | 3 | 0xFFFF
Not applicable | 51836 | CA7C | 1 | harmonic V2 row 49 | 0.1% | 3 | 0xFFFF
Not applicable | 51837 | CA7D | 1 | harmonic V3 row 49 | 0.1% | 3 | 0xFFFF
Not applicable | 51838 | CA7E | 1 | harmonic V1 row 51 | 0.1% | 3 | 0xFFFF
Not applicable | 51839 | CA7F | 1 | harmonic V2 row 51 | 0.1% | 3 | 0xFFFF
Not applicable | 51840 | CA80 | 1 | harmonic V3 row 51 | 0.1% | 3 | 0xFFFF
Not applicable | 51841 | CA81 | 1 | harmonic V1 row 53 | 0.1% | 3 | 0xFFFF
Not applicable | 51842 | CA82 | 1 | harmonic V2 row 53 | 0.1% | 3 | 0xFFFF
Not applicable | 51843 | CA83 | 1 | harmonic V3 row 53 | 0.1% | 3 | 0xFFFF
Not applicable | 51844 | CA84 | 1 | harmonic V1 row 55 | 0.1% | 3 | 0xFFFF
Not applicable | 51845 | CA85 | 1 | harmonic V2 row 55 | 0.1% | 3 | 0xFFFF
Not applicable | 51846 | CA86 | 1 | harmonic V3 row 55 | 0.1% | 3 | 0xFFFF
Not applicable | 51847 | CA87 | 1 | harmonic V1 row 57 | 0.1% | 3 | 0xFFFF
Not applicable | 51848 | CA88 | 1 | harmonic V2 row 57 | 0.1% | 3 | 0xFFFF
Not applicable | 51849 | CA89 | 1 | harmonic V3 row 57 | 0.1% | 3 | 0xFFFF
Not applicable | 51850 | CA8A | 1 | harmonic V1 row 59 | 0.1% | 3 | 0xFFFF
Not applicable | 51851 | CA8B | 1 | harmonic V2 row 59 | 0.1% | 3 | 0xFFFF
Not applicable | 51852 | CA8C | 1 | harmonic V3 row 59 | 0.1% | 3 | 0xFFFF
Not applicable | 51853 | CA8D | 1 | harmonic V1 row 61 | 0.1% | 3 | 0xFFFF
Not applicable | 51854 | CA8E | 1 | harmonic V2 row 61 | 0.1% | 3 | 0xFFFF
Not applicable | 51855 | CA8F | 1 | harmonic V3 row 61 | 0.1% | 3 | 0xFFFF
Not applicable | 51856 | CA90 | 1 | harmonic V1 row 63 | 0.1% | 3 | 0xFFFF
Not applicable | 51857 | CA91 | 1 | harmonic V2 row 63 | 0.1% | 3 | 0xFFFF
Not applicable | 51858 | CA92 | 1 | harmonic V3 row 63 | 0.1% | 3 | 0xFFFF
| 51765 | CA35 | 94
| 51536 | C950 | 323
E000 Hex : Network Setting
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 57344 | E000 | 1 | Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL 6 : 2BL | – | 3,6,16 | 0xFFFF
| 57345 | E001 | 1 | Current Transformer secondary : 1: 1 A 5: 5 A | A | 3,6,16 | 0xFFFF
| 57346 | E002 | 1 | Current Transformer primary | A | 3,6,16 | 0xFFFF
Not applicable | 57347 | E003 | 1 | Neutral Current Transformer present : 0 : No 1: Yes | – | 3,6,16 | 0xFFFF
Not applicable | 57348 | E004 | 1 | Neutral Current Transformer secondary: 1: 1 A 5: 5 A | A | 3,6,16 | 0xFFFF
Not applicable | 57349 | E005 | 1 | Neutral Current Transformer primary | A | 3,6,16 | 0xFFFF
Not applicable | 57350 | E006 | 1 | Voltage transformer present : 0 : No 1: Yes | – | 3,6,16 | 0xFFFF
Not applicable | 57351 | E007 | 1 | Voltage Transformersecondary : 60 : 60 V 100 : 100 V 110 : 110 V 115 : 115 V 120 : 120 V 173 : 173 V 190 : 190 V | V | 3,6,16 | 0xFFFF
Not applicable | 57352 | E008 | 2 | Voltage Transformer primary | V | 3,6,16 | 0xFFFFFFFF
Not applicable | 57354 | E00A | 1 | Internal/External Top | 0:internal / 1:external | 3,6,16 | 0xFFFF
Not applicable | 57355 | E00B | 1 | Synchronisation Top for P+/- Q+/- : time in seconds ( 2mn, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) | secondes | 3,6,16 | 0xFFFF
| 57344 | E000 | 12
E200 Hex : Action system ( Write Function only )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57856 | E200 | 1 | Action : 0xA1 : Product Configuration storage 0xB2 : Produit reboot |  | 6
| 57856 | E200 | 1
SM101C specific tables
8D50 Hex : Alarme
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 36176 | 8D50 | 1 | Current alarm on lower threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 31 : ∑PFC / 32 : T°C 1 | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 31: - 32 : °C/10 | 3
| 36177 | 8D51 | 2 | Current alarm on lower threshold : min value | - | 3
| 36179 | 8D53 | 1 | Current alarm on upper threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 31 : ∑PFC / 32 : T°C 1 | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 31: - 32 : °C/10 | 3
| 36180 | 8D54 | 2 | Current alarm on upper threshold : max value | - | 3
| 36182 | 8D56 | 1 | Current alarm duration | s | 3
| 36176 | 8D50 | 7
8E00 Hex : Table Setup
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 36352 | 8E00 | 1 | Network : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL | / | 3,6,16
| 36353 | 8E01 | 1 | Current Transformer secondary : 1: 1 A 5: 5 A | A | 3,6,16
| 36354 | 8E02 | 1 | Current Transformer primary | A | 3,6,16
| 36355 | 8E03 | 1 | Reserved |  | 3,6,16
| 36356 | 8E04 | 1 | Synchronisation of I AVG/MAX: 2 : 2 seconds 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes | / | 3,6,16
| 36357 | 8E05 | 1 | Synchronisation of P/Q/S AVG/MAX 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes | / | 3,6,16
| 36358 | 8E06 | 1 | OUT 1 : pulse output allocation : 0 : kWh+ 1 : kvarh + 2 :Alarm 3 : Command | / | 3,6,16
| 36359 | 8E07 | 1 | OUT 1 : pulse output value : 0 : 0,1 kWh/kvarh 1 : 1 kWh/kvarh 2 : 10 kWh/kvarh 3 : 100 kWh/kvarh 4 : 1000 kWh/kvarh 5 : 10000 kWh/kvarh |  | 3,6,16
| 36360 | 8E08 | 1 | OUT 1 : pulse output duration : 1 : 100ms - 2 : 200ms 3 : 300ms - 4 : 400ms 5 : 500ms - 6 : 600ms 7 : 700ms - 8 : 800ms 9 : 900ms |  | 3,6,16
| 36361 | 8E09 | 1 | Hour meter allocation 1 : Auxiliary power supply 2 : Currents 3 : phase to phase voltage |  | 3,6,16
| 36362 | 8E0A | 1 | Hour meter trigger threshold | A/V | 3,6,16
| 36363 | 8E0B | 1 | Alarm Type : 1 : I 2 : In 3 : U 4 : V 5 : ∑P+ 6 : ∑Q+ 7 : ∑S+ 8 : ∑PFC 9 : ∑PFL 5 : P 6 : Q 7 : S 8 : CPF 9 : LPF 10 : THDU 11 : THDV 12 : THDI 13 : HOUR 14 : F 15 : Internal temperature |  | 3,6,16
| 36364 | 8E0C | 1 | Alarm Specified time (0-999) |  | 3,6,16
| 36365 | 8E0D | 1 | Alarm upper Threshold |  | 3,6,16
| 36366 | 8E0E | 1 | Alarm Lower Threshold |  | 3,6,16
| 36367 | 8E0F | 1 | Alarm Hysteresis(0-99) |  | 3,6,16
| 36368 | 8E10 | 1 | Relay State : 0 : Open 1 : Closed |  | 3,6,16
| 36352 | 8E00 | 17
400 Hex : Reset ( These values could be combine all )
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 1024 | 400 | 1 | Reset : Max 4I : 0x1 Max P+,Q+,S : 0x2 kWh+ : 0x80 kvarh+ : 0x100 tous les paramètres : 0x1000 | / | 6
| 1024 | 400 | 1
C691 Hex : Energy meters residual values (current kWh & kvarh)
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 50833 | C691 | 1 | Ea+ Residual | 0,01 kWh | 3
| 50834 | C692 | 1 | Er+ Residual | 0,01 kvarh | 3
| 50835 | C693 | 1 | Dummy |  | 3
| 50836 | C694 | 1 | Dummy |  | 3
| 50837 | C695 | 1 | Dummy |  | 3
| 50833 | C691 | 5
1000 Hex : Customization specific data
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 4096 | 1000 | 1 | Customisation specific data loaded 0x0000 : FALSE 0x0001 : TRUE |  | 3
| 4097 | 1001 | 1 | Retrofit activated 0x0000 : FALSE 0x0001 : TRUE |  | 3
| 4098 | 1002 | 8 | TC list : TC 1 / TC2 / TC3 / TC4 / TC5 / TC6 / TC7 / TC8 | A | 3
| 4106 | 100A | 16 | TC gain correction X1 2 words = 1 TC correction |  | 3
| 4122 | 101A | 16 | TC gain correction X2 2 words = 1 TC correction |  | 3

## Application Notes
APPLICATION NOTES
Historical data principle
The historical data can be read in two steps :
1 : Set the read pointer ( Write in the R1 register )
2 : Read the data buffer ( Read from the R2 register )
Command Area : Register R1 : Size 1 word
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| R1 ( DEC) | R1 ( Hex) | 1 | Actions : 0x0001 : Reset reader pointer : locate the pointer on the most recent value stored 0xFFFE : Get Next data packet ( pointer is updated ) |  | W
| R1 | R1 | 1
When the register R1 is writing with the value 1 : automaticaly the data buffer ( Regsiter R2 ) is filled with the most recent value stored
After this operation, to read the next data Write 0XFFFE in the register R1
Data Area : Register R2 = R1 +10Hex : ( size 125 Words )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
Header | R2(DEC) | R2(HEX) | 1 | Record count |  | R
| R2 +1 | R2 +1 | 1 | Record size : Y |  | R
| R2 +2 | R2 +2 | x | Data Header : this header may not exist according the historical type |  | R
Data Buffer | R3=R2 + 2 + x | R3=R2 + 2 + x | Y | Data |  | R
| R3 + Y | R3 + Y | Y | Data |  | R
| … | … | Y | Data |  | R
| …. | … | Y | Data |  | R
| R3+ n * Y | R3+ n * Y | Y | Data |  | R
The data area start always by two words :
1 : Record count : number of record present in the buffer
2 : Record Size : size of one data
Always read the complete area : function 16 with 125 Words
EN50160 Classification values
Sag classification
Duration t [ms]
Residual voltage u [%] | 20 < t < 200 | 200 < t < 500 | 500 < t < 1000 | 1000 < t < 5000 | 5000 < t <60000
90 > u >= 80 | 1 | 2 | 3 | 4 | 5
80 > u >= 70 | 6 | 7 | 8 | 9 | 10
70 > u >= 40 | 11 | 12 | 13 | 14 | 15
40 > u >= 5 | 16 | 17 | 18 | 19 | 20
5 > u | 21 | 22 | 23 | 24 | 25
Swell classification
Duration t [ms]
Swell voltage u [%] | 20 < t < 500 | 500 < t < 5000 | 5000 < t < 60000
u >= 120 | 26 | 27 | 28
120 > u >= 110 | 29 | 30 | 31