## 6LE005455Aa
|  | ECM01 Modbus Registers | [6 empty] | MOD007 V01
Modbus Parameters |  |  |  |  | Default
Mode: | RTU (LSB first, apply address offset of +1 for Function 3 Holding Registers)
Baudrate: | 300 / 600 / 1200 / 2400 / 4800 / 9600 / 19200 bps |  |  |  | 9600
Data Bit: | 8
Stop Bits: | 1 or 2 |  |  |  | 1
Parity: | None / Odd / Even |  |  |  | None
Functions: | 3 / 4
Scan Rate: | ≤ 100mS
Register List
Starting Address (Decimal) | Starting Register (Hex) | Parameter | Unit | Function | Read / Write | Length | Data structure | Range / Value | Default
30000 | 0x00 | Voltage V1-N | V | 3 | R | 2 | Float | - | -
30002 | 0x02 | Voltage V2-N | V | 3 | R | 2 | Float | - | -
30004 | 0x04 | Voltage V3-N | V | 3 | R | 2 | Float | - | -
30006 | 0x06 | Average Voltage L-N | V | 3 | R | 2 | Float | - | -
30008 | 0x08 | Voltage V1-2 | V | 3 | R | 2 | Float | - | -
30010 | 0x0A | Voltage V2-3 | V | 3 | R | 2 | Float | - | -
30012 | 0x0C | Voltage V3-1 | V | 3 | R | 2 | Float | - | -
30014 | 0x0E | Average Voltage L-L | V | 3 | R | 2 | Float | - | -
30016 | 0x10 | Current I1 | A | 3 | R | 2 | Float | - | -
30018 | 0x12 | Current I2 | A | 3 | R | 2 | Float | - | -
30020 | 0x14 | Current I3 | A | 3 | R | 2 | Float | - | -
30022 | 0x16 | Average Current | A | 3 | R | 2 | Float | - | -
30024 | 0x18 | kW1 | kW | 3 | R | 2 | Float | - | -
30026 | 0x1A | kW2 | kW | 3 | R | 2 | Float | - | -
30028 | 0x1C | kW3 | kW | 3 | R | 2 | Float | - | -
30030 | 0x1E | kVA1 | kVA | 3 | R | 2 | Float | - | -
30032 | 0x20 | kVA2 | kVA | 3 | R | 2 | Float | - | -
30034 | 0x22 | kVA3 | kVA | 3 | R | 2 | Float | - | -
30036 | 0x24 | kVAr1 | kVAr | 3 | R | 2 | Float | - | -
30038 | 0x26 | kVAr2 | kVAr | 3 | R | 2 | Float | - | -
30040 | 0x28 | kVAr3 | kVAr | 3 | R | 2 | Float | - | -
30042 | 0x2A | Total kW | kW | 3 | R | 2 | Float | - | -
30044 | 0x2C | Total kVA | kVA | 3 | R | 2 | Float | - | -
30046 | 0x2E | Total kVAr | kVAr | 3 | R | 2 | Float | - | -
30048 | 0x30 | PF1 |  | 3 | R | 2 | Float | - | -
30050 | 0x32 | PF2 |  | 3 | R | 2 | Float | - | -
30052 | 0x34 | PF3 |  | 3 | R | 2 | Float | - | -
30054 | 0x36 | Average PF |  | 3 | R | 2 | Float | - | -
30056 | 0x38 | Frequency | Hz | 3 | R | 2 | Float | - | -
30058 | 0x3A | Total net kWh | kWh | 3 | R | 2 | Float | - | -
30060 | 0x3C | Total net kVAh | kVAh | 3 | R | 2 | Float | - | -
30062 | 0x3E | Total net kVArh | kVArh | 3 | R | 2 | Float | - | -
30064 | 0x40 | kW Max Active Power | kW | 3 | R | 2 | Float | - | -
30066 | 0x42 | kW Min Active Power | kW | 3 | R | 2 | Float | - | -
30068 | 0x44 | kVAr Max Reactive Power | kVAr | 3 | R | 2 | Float | - | -
30070 | 0x46 | kVAr Min Reactive Power | kVAr | 3 | R | 2 | Float | - | -
30072 | 0x48 | kVA Max Apparent Power | kVA | 3 | R | 2 | Float | - | -
30074 | 0x4A | Max I1 Current Demand | A | 3 | R | 2 | Float | - | -
30076 | 0x4B | Max I2 Current Demand | A | 3 | R | 2 | Float | - | -
30078 | 0x4E | Max I3 Current Demand | A | 3 | R | 2 | Float | - | -
30080 | 0x50 | Max Average Current Demand | A | 3 | R | 2 | Float | - | -
30082 | 0x52 | Run hour | hrs | 3 | R | 2 | Float | - | -
30084 | 0x54 | kWh1 (Imp) | kWh | 3 | R | 2 | Float | - | -
30086 | 0x56 | kWh2 (Imp) | kWh | 3 | R | 2 | Float | - | -
30088 | 0x58 | kWh3 (Imp) | kWh | 3 | R | 2 | Float | - | -
30090 | 0x5A | kW1 (Exp) | kWh | 3 | R | 2 | Float | - | -
30092 | 0x5C | kW2 (Exp) | kWh | 3 | R | 2 | Float | - | -
30094 | 0x5E | kW3 (Exp) | kWh | 3 | R | 2 | Float | - | -
30096 | 0x60 | Total kWh (Imp) | kWh | 3 | R | 2 | Float | - | -
30098 | 0x62 | Total kWh (Exp) | kWh | 3 | R | 2 | Float | - | -
30100 | 0x64 | kVArh1 (Imp) | kVArh | 3 | R | 2 | Float | - | -
30102 | 0x66 | kVArh2 (Imp) | kVArh | 3 | R | 2 | Float | - | -
30104 | 0x68 | kVArh3 (Imp) | kVArh | 3 | R | 2 | Float | - | -
30106 | 0x6A | kVArh1 (Exp) | kVArh | 3 | R | 2 | Float | - | -
30108 | 0x6C | kVArh2 (Exp) | kVArh | 3 | R | 2 | Float | - | -
30110 | 0x6E | kVArh3 (Exp) | kVArh | 3 | R | 2 | Float | - | -
30112 | 0x70 | Total kVArh (Imp) | kVArh | 3 | R | 2 | Float | - | -
30114 | 0x72 | Total kVArh (Exp) | kVArh | 3 | R | 2 | Float | - | -
30116 | 0x74 | kVAh1 | kVAh | 3 | R | 2 | Float | - | -
30118 | 0x76 | kVAh2 | kVAh | 3 | R | 2 | Float | - | -
30120 | 0x78 | kVAh3 | kVAh | 3 | R | 2 | Float | - | -
30122 | 0x7A | Neutral Current | A | 3 | R | 2 | Float | - | -
30124 | 0x7C | THD of 1st Phase Voltage | % | 3 | R | 2 | Float | - | -
30126 | 0x7E | THD of 2nd Phase Voltage | % | 3 | R | 2 | Float | - | -
30128 | 0x80 | THD of 3rd Phase Voltage | % | 3 | R | 2 | Float | - | -
30130 | 0x82 | THD of Voltage V1-2 | % | 3 | R | 2 | Float | - | -
30132 | 0x84 | THD of Voltage V2-3 | % | 3 | R | 2 | Float | - | -
30134 | 0x86 | THD of Voltage V3-1 | % | 3 | R | 2 | Float | - | -
30136 | 0x88 | THD of Current I1 | % | 3 | R | 2 | Float | - | -
30138 | 0x8A | THD of Current I2 | % | 3 | R | 2 | Float | - | -
30140 | 0x8C | THD of Current I3 | % | 3 | R | 2 | Float | - | -
30684 | 0x2AC | Serial No. |  | 3 | R | 2 | Hex | - | -
30700 | 0x2BC | Phase Sequence Indicator |  | 3 | R | 2 | Integer | 0: Clockwise 1: Anticlockwise 2: Invalid | -
30702 | 0x2BE | Existing kW Max Active Power | kW | 3 | R | 2 | Float | - | -
30704 | 0x2C0 | Existing kW Min Active Power | kW | 3 | R | 2 | Float | - | -
30706 | 0x2C2 | Existing kVAr Max Reactive Power | kVAr | 3 | R | 2 | Float | - | -
30708 | 0x2C4 | Existing kVAr Min Reactive Power | kVAr | 3 | R | 2 | Float | - | -
30710 | 0x2C6 | Existing kVA Max Apparent Power | kVA | 3 | R | 2 | Float | - | -
30712 | 0x2C8 | Existing Max I1 Demand | A | 3 | R | 2 | Float | - | -
30714 | 0x2CA | Existing Max I2 Demand | A | 3 | R | 2 | Float | - | -
30716 | 0x2CC | Existing Max I3 Demand | A | 3 | R | 2 | Float | - | -
30718 | 0x2CE | Existing Max Avg. Current Demand | A | 3 | R | 2 | Float | - | -
40000 | 0x00 | Password |  | 4 | R/W | 1 | Integer | 0000 - 9998 | 1000
40001 | 0x01 | Network Selection |  | 4 | R/W | 1 | Integer | 0x0000: 3P4W 0x0002: 1P2W-P1 0x0003: 1P2W-P2 0x0004: 1P2W-P3 | 0x0000
40002 | 0x02 | CT Secondary | A | 4 | R | 1 | Integer | 5 | 5
40003 | 0x03 | CT Primary | A | 4 | R/W | 1 | Integer | 5 - 10000 | 160
40004 | 0x04 | PT Secondary | V | 4 | R/W | 1 | Integer | 173 - 415 | 350
40005 | 0x05 | PT Primary | V | 4 | R/W | 2 | Integer | 100 - 500k | 350
40007 | 0x07 | Slave ID |  | 4 | R/W | 1 | Integer | 1 - 255 | 1
40008 | 0x08 | Baud Rate | bps | 4 | R/W | 1 | Integer | 0x0000: 300 0x0002: 600 0x0003: 2400 0x0004: 4800 0x0005: 9600 0x0006: 19200 | 0x0005
40009 | 0x09 | Parity |  | 4 | R/W | 1 | Integer | 0x0000: None 0x0001: Odd 0x0002: Even | 0x0000
40010 | 0x0A | Stop Bit |  | 4 | R/W | 1 | Integer | 0x0000: 1 0x0001: 2 | 0x0000
40011 | 0x0B | Backlight OFF | sec | 4 | R/W | 1 | Integer | 0 - 7200 | 0
40012 | 0x0C | Factory Default |  | 4 | R/W | 1 | Integer | 1: Set to factory setting range | -
40016 | 0x10 | Auto Mode Pages |  | 4 | R/W | 1 | Integer | 1 - 21 | 21
40017 | 0x11 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40018 | 0x12 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40019 | 0x13 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40020 | 0x14 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40021 | 0x15 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40022 | 0x16 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40023 | 0x17 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40024 | 0x18 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40025 | 0x19 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40026 | 0x1A | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40027 | 0x1B | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40028 | 0x1C | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40029 | 0x1D | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40030 | 0x1E | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40031 | 0x1F | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40032 | 0x20 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40033 | 0x21 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40034 | 0x22 | Demand Interval Method |  | 4 | R/W | 1 | Integer | 0x0000: Sliding 0x0001: Fixed | 0x0000
40035 | 0x23 | Demand Interval Duration |  | 4 | R/W | 1 | Integer | 1 - 30 | 15
40036 | 0x24 | Demand Interval Length | min | 4 | R/W | 1 | Integer | 1 - 30 | 1
40043 | 0x2B | Reset Max Power |  | 4 | R/W | 1 | Integer | 1: Reset all max power | -
40044 | 0x2C | Reset Energy Values |  | 4 | R/W | 1 | Integer | 1: Reset all energy values | -
40045 | 0x2D | Reset Run Hour |  | 4 | R/W | 1 | Integer | 1: Reset run hour | -
40054 | 0x36 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40055 | 0x37 | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40057 | 0x39 | Pulse Duration | sec | 4 | R/W | 1 | Integer | 0.1 - 2.0 | 0.1
40058 | 0x3A | Pulse Weight | kWh | 4 | R/W | 1 | Integer | 0.01 - 99.99 | 0.1
40059 | 0x3B | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40060 | 0x3C | Page Address Sequence |  | 4 | R/W | 1 | Integer | 1-21 / 1-First Page; 21-Last Page | -
40063 | 0x3F | Reset Max Current |  | 4 | R/W | 1 | Integer | 1: Reset max current | -