## Identification
Device Identification
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Device Vendor Name | - | - | 4096 | 1000 | 16 | STRING | H'03' | "Hager" : Hex 48 61 67 65 72 | X | X | X
Device Product code | - | - | 4112 | 1010 | 16 | STRING | H'03' | Example: "AXX516D": Hex 41 58 58 35 31 36 44 | X | X | X
Device SW version | - | - | 4128 | 1020 | 2 | U32 | H'03' | Example: v1.2.2 : Hex 01 02 02 00 | X | X | X
Device Vendor URL | - | - | 4130 | 1022 | 16 | STRING | H'03' | "https://hager.com" | X | X | X
Device Product name | - | - | 4146 | 1032 | 16 | STRING | H'03' | "Digital Protection Device" | X | X | X
Device Model name | - | - | 4162 | 1042 | 16 | STRING | H'03' | "Digital Protection Device" | X | X | X
Device User application name | - | - | 4178 | 1052 | 16 | STRING | H'03' | "APL" | X | X | X
Device Serial number | - | - | 4196 | 1064 | 16 | STRING | H'03' |  | X | X | X
Device Product version | - | - | 4216 | 1078 | 2 | U32 | H'03' | Example: v1.2.2 : Hex 01 02 02 00 | X | X | X
Device Communication version | - | - | 4218 | 107A | 2 | U32 | H'03' | Example: v1.2.2 : Hex 01 02 02 00 | X | X | X
Device Modbus version | - | - | 4220 | 107C | 2 | U32 | H'03' | Example: v1.2.2 : Hex 01 02 02 00 | X | X | X
Device Date Code | - | - | 8240 | 2030 | 8 | STRING | H'03' | YYYYMMDD | X | X | X
Device Short UID | - | - | 8267 | 204B | 11 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X | X | X

## Information
Device Information
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
User Date & time | s | 1 | 8448 | 2100 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X | X | X
Device Commissioned State | - | - | 24576 | 6000 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed |  | X | X
Device Communication Status | - | - | 24577 | 6001 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device |  | X | X
Device Short UID configured | - | - | 24578 | 6002 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" |  | X | X
Device Wireless UID | - | - | 24594 | 6012 | 4 | U64 | H'03' |  |  | X | X
Device Commissioned Date | s | 1 | 24598 | 6016 | 2 | U32 | H'03' | Time in second since 1st January 2000 |  | X | X
Device Communication Status update date & time | s | 1 | 24600 | 6018 | 2 | U32 | H'03' | Time in second since 1st January 2000 |  | X | X
Device Last Message RSSI | - | - | 24604 | 601C | 1 | U16 | H'03' |  |  | X | X
Slave 1 Commissioned State | - | - | 32768 | 8000 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 1 Communication Status | - | - | 32769 | 8001 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 1 Short UID configured | - | - | 32770 | 8002 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 1 Wireless UID | - | - | 32786 | 8012 | 4 | U64 | H'03' |  | X
Slave 1 Commissioned Date | s | 1 | 32790 | 8016 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 1 Communication Status update date & time | s | 1 | 32792 | 8018 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 1 Last Message RSSI | - | - | 32796 | 801C | 1 | U16 | H'03' |  | X
Slave 2 Commissioned State | - | - | 32896 | 8080 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 2 Communication Status | - | - | 32897 | 8081 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 2 Short UID configured | - | - | 32898 | 8082 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 2 Wireless UID | - | - | 32914 | 8092 | 4 | U64 | H'03' |  | X
Slave 2 Commissioned Date | s | 1 | 32918 | 8096 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 2 Communication Status update date & time | s | 1 | 32920 | 8098 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 2 Last Message RSSI | - | - | 32924 | 809C | 1 | U16 | H'03' |  | X
Slave 3 Commissioned State | - | - | 33024 | 8100 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 3 Communication Status | - | - | 33025 | 8101 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 3 Short UID configured | - | - | 33042 | 8102 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 3 Wireless UID | - | - | 33042 | 8112 | 4 | U64 | H'03' |  | X
Slave 3 Commissioned Date | s | 1 | 33046 | 8116 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 3 Communication Status update date & time | s | 1 | 33048 | 8118 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 3 Last Message RSSI | - | - | 33052 | 811C | 1 | U16 | H'03' |  | X
Slave 4 Commissioned State | - | - | 33152 | 8180 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 4 Communication Status | - | - | 33153 | 8181 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 4 Short UID configured | - | - | 33154 | 8182 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 4 Wireless UID | - | - | 33170 | 8192 | 4 | U64 | H'03' |  | X
Slave 4 Commissioned Date | s | 1 | 33174 | 8196 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 4 Communication Status update date & time | s | 1 | 33176 | 8198 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 4 Last Message RSSI | - | - | 33180 | 819C | 1 | U16 | H'03' |  | X
Slave 5 Commissioned State | - | - | 33280 | 8200 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 5 Communication Status | - | - | 33281 | 8201 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 5 Short UID configured | - | - | 33282 | 8202 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 5 Wireless UID | - | - | 33298 | 8212 | 4 | U64 | H'03' |  | X
Slave 5 Commissioned Date | s | 1 | 33302 | 8216 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 5 Communication Status update date & time | s | 1 | 33304 | 8218 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 5 Last Message RSSI | - | - | 33308 | 821C | 1 | U16 | H'03' |  | X
Slave 6 Commissioned State | - | - | 33408 | 8280 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 6 Communication Status | - | - | 33409 | 8281 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 6 Short UID configured | - | - | 33410 | 8282 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 6 Wireless UID | - | - | 33426 | 8292 | 4 | U64 | H'03' |  | X
Slave 6 Commissioned Date | s | 1 | 33430 | 8296 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 6 Communication Status update date & time | s | 1 | 33432 | 8298 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 6 Last Message RSSI | - | - | 33436 | 829C | 1 | U16 | H'03' |  | X
Slave 7 Commissioned State | - | - | 33536 | 8300 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 7 Communication Status | - | - | 33537 | 8301 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 7 Short UID configured | - | - | 33538 | 8302 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 7 Wireless UID | - | - | 33554 | 8312 | 4 | U64 | H'03' |  | X
Slave 7 Commissioned Date | s | 1 | 33558 | 8316 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 7 Communication Status update date & time | s | 1 | 33560 | 8318 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 7 Last Message RSSI | - | - | 33564 | 831C | 1 | U16 | H'03' |  | X
Slave 8 Commissioned State | - | - | 33664 | 8380 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 8 Communication Status | - | - | 33665 | 8381 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 8 Short UID configured | - | - | 33666 | 8382 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 8 Wireless UID | - | - | 33682 | 8392 | 4 | U64 | H'03' |  | X
Slave 8 Commissioned Date | s | 1 | 33686 | 8396 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 8 Communication Status update date & time | s | 1 | 33688 | 8398 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 8 Last Message RSSI | - | - | 33692 | 839C | 1 | U16 | H'03' |  | X
Slave 9 Commissioned State | - | - | 33792 | 8400 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 9 Communication Status | - | - | 33793 | 8401 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 9 Short UID configured | - | - | 33794 | 8402 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 9 Wireless UID | - | - | 33810 | 8412 | 4 | U64 | H'03' |  | X
Slave 9 Commissioned Date | s | 1 | 33814 | 8416 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 9 Communication Status update date & time | s | 1 | 33816 | 8418 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 9 Last Message RSSI | - | - | 33820 | 841C | 1 | U16 | H'03' |  | X
Slave 10 Commissioned State | - | - | 33920 | 8480 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 10 Communication Status | - | - | 33921 | 8481 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 10 Short UID configured | - | - | 33922 | 8482 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 10 Wireless UID | - | - | 33938 | 8492 | 4 | U64 | H'03' |  | X
Slave 10 Commissioned Date | s | 1 | 33942 | 8496 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 10 Communication Status update date & time | s | 1 | 33944 | 8498 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 10 Last Message RSSI | - | - | 33948 | 849C | 1 | U16 | H'03' |  | X
Slave 11 Commissioned State | - | - | 34048 | 8500 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 11 Communication Status | - | - | 34049 | 8501 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 11 Short UID configured | - | - | 34050 | 8502 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 11 Wireless UID | - | - | 34066 | 8512 | 4 | U64 | H'03' |  | X
Slave 11 Commissioned Date | s | 1 | 34070 | 8516 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 11 Communication Status update date & time | s | 1 | 34072 | 8518 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 11 Last Message RSSI | - | - | 34076 | 851C | 1 | U16 | H'03' |  | X
Slave 12 Commissioned State | - | - | 34176 | 8580 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 12 Communication Status | - | - | 34177 | 8581 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 12 Short UID configured | - | - | 34178 | 8582 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 12 Wireless UID | - | - | 34194 | 8592 | 4 | U64 | H'03' |  | X
Slave 12 Commissioned Date | s | 1 | 34198 | 8596 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 12 Communication Status update date & time | s | 1 | 34200 | 8598 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 12 Last Message RSSI | - | - | 34204 | 859C | 1 | U16 | H'03' |  | X
Slave 13 Commissioned State | - | - | 34304 | 8600 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 13 Communication Status | - | - | 34305 | 8601 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 13 Short UID configured | - | - | 34306 | 8602 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 13 Wireless UID | - | - | 34322 | 8612 | 4 | U64 | H'03' |  | X
Slave 13 Commissioned Date | s | 1 | 34326 | 8616 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 13 Communication Status update date & time | s | 1 | 34328 | 8618 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 13 Last Message RSSI | - | - | 34332 | 861C | 1 | U16 | H'03' |  | X
Slave 14 Commissioned State | - | - | 34432 | 8680 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 14 Communication Status | - | - | 34433 | 8681 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 14 Short UID configured | - | - | 34434 | 8682 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 14 Wireless UID | - | - | 34450 | 8692 | 4 | U64 | H'03' |  | X
Slave 14 Commissioned Date | s | 1 | 34454 | 8696 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 14 Communication Status update date & time | s | 1 | 34456 | 8698 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 14 Last Message RSSI | - | - | 34460 | 869C | 1 | U16 | H'03' |  | X
Slave 15 Commissioned State | - | - | 34560 | 8700 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 15 Communication Status | - | - | 34561 | 8701 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 15 Short UID configured | - | - | 34562 | 8702 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 15 Wireless UID | - | - | 34578 | 8712 | 4 | U64 | H'03' |  | X
Slave 15 Commissioned Date | s | 1 | 34582 | 8716 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 15 Communication Status update date & time | s | 1 | 34584 | 8718 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 15 Last Message RSSI | - | - | 34588 | 871C | 1 | U16 | H'03' |  | X
Slave 16 Commissioned State | - | - | 34688 | 8780 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 16 Communication Status | - | - | 34689 | 8781 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 16 Short UID configured | - | - | 34690 | 8782 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 16 Wireless UID | - | - | 34706 | 8792 | 4 | U64 | H'03' |  | X
Slave 16 Commissioned Date | s | 1 | 34710 | 8796 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 16 Communication Status update date & time | s | 1 | 34712 | 8798 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 16 Last Message RSSI | - | - | 34716 | 879C | 1 | U16 | H'03' |  | X
Slave 17 Commissioned State | - | - | 34816 | 8800 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 17 Communication Status | - | - | 34817 | 8801 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 17 Short UID configured | - | - | 34818 | 8802 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 17 Wireless UID | - | - | 34834 | 8812 | 4 | U64 | H'03' |  | X
Slave 17 Commissioned Date | s | 1 | 34838 | 8816 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 17 Communication Status update date & time | s | 1 | 34840 | 8818 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 17 Last Message RSSI | - | - | 34844 | 881C | 1 | U16 | H'03' |  | X
Slave 18 Commissioned State | - | - | 34944 | 8880 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 18 Communication Status | - | - | 34945 | 8881 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 18 Short UID configured | - | - | 34946 | 8882 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 18 Wireless UID | - | - | 34962 | 8892 | 4 | U64 | H'03' |  | X
Slave 18 Commissioned Date | s | 1 | 34966 | 8896 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 18 Communication Status update date & time | s | 1 | 34968 | 8898 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 18 Last Message RSSI | - | - | 34972 | 889C | 1 | U16 | H'03' |  | X
Slave 19 Commissioned State | - | - | 35072 | 8900 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 19 Communication Status | - | - | 35073 | 8901 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 19 Short UID configured | - | - | 35074 | 8902 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 19 Wireless UID | - | - | 35090 | 8912 | 4 | U64 | H'03' |  | X
Slave 19 Commissioned Date | s | 1 | 35094 | 8916 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 19 Communication Status update date & time | s | 1 | 35096 | 8918 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 19 Last Message RSSI | - | - | 35100 | 891C | 1 | U16 | H'03' |  | X
Slave 20 Commissioned State | - | - | 35200 | 8980 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 20 Communication Status | - | - | 35201 | 8981 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 20 Short UID configured | - | - | 35202 | 8982 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 20 Wireless UID | - | - | 35218 | 8992 | 4 | U64 | H'03' |  | X
Slave 20 Commissioned Date | s | 1 | 35222 | 8996 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 20 Communication Status update date & time | s | 1 | 35224 | 8998 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 20 Last Message RSSI | - | - | 35228 | 899C | 1 | U16 | H'03' |  | X
Slave 21 Commissioned State | - | - | 35328 | 8A00 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 21 Communication Status | - | - | 35329 | 8A01 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 21 Short UID configured | - | - | 35330 | 8A02 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 21 Wireless UID | - | - | 35346 | 8A12 | 4 | U64 | H'03' |  | X
Slave 21 Commissioned Date | s | 1 | 35350 | 8A16 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 21 Communication Status update date & time | s | 1 | 35352 | 8A18 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 21 Last Message RSSI | - | - | 35356 | 8A1C | 1 | U16 | H'03' |  | X
Slave 22 Commissioned State | - | - | 35456 | 8A80 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 22 Communication Status | - | - | 35457 | 8A81 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 22 Short UID configured | - | - | 35458 | 8A82 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 22 Wireless UID | - | - | 35474 | 8A92 | 4 | U64 | H'03' |  | X
Slave 22 Commissioned Date | s | 1 | 35478 | 8A96 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 22 Communication Status update date & time | s | 1 | 35480 | 8A98 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 22 Last Message RSSI | - | - | 35484 | 8A9C | 1 | U16 | H'03' |  | X
Slave 23 Commissioned State | - | - | 35584 | 8B00 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 23 Communication Status | - | - | 35585 | 8B01 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 23 Short UID configured | - | - | 35586 | 8B02 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 23 Wireless UID | - | - | 35602 | 8B12 | 4 | U64 | H'03' |  | X
Slave 23 Commissioned Date | s | 1 | 35606 | 8B16 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 23 Communication Status update date & time | s | 1 | 35608 | 8B18 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 23 Last Message RSSI | - | - | 35612 | 8B1C | 1 | U16 | H'03' |  | X
Slave 24 Commissioned State | - | - | 35712 | 8B80 | 1 | U16 | H'03' | Hex 00 00 = Free Hex 00 01 = Device Pairing in progress Hex 00 02 = Device Paired Hex 00 03 = Device unpairing in progress Hex 00 04 = Device Unpaired Hex 00 05 = Device Pairing Failed Hex 00 06 = Device Unpairing Failed | X
Slave 24 Communication Status | - | - | 35713 | 8B81 | 1 | U16 | H'03' | Hex 00 00 = Unitialized Hex 00 01 = Device Synchronized Hex 00 02 = Device Not Responding Hex 00 04 = Unsupported Device | X
Slave 24 Short UID configured | - | - | 35714 | 8B82 | 16 | STRING | H'03' | Example : "E26ccJLxLWf8TTJLsKZ2EY" | X
Slave 24 Wireless UID | - | - | 35730 | 8B92 | 4 | U64 | H'03' |  | X
Slave 24 Commissioned Date | s | 1 | 35734 | 8B96 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 24 Communication Status update date & time | s | 1 | 35736 | 8B98 | 2 | U32 | H'03' | Time in second since 1st January 2000 | X
Slave 24 Last Message RSSI | - | - | 35740 | 8B9C | 1 | U16 | H'03' |  | X

## Configuration
Configuration
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
DHCP enable | - | - | 28672 | 7000 | 1 | U16 | H'03' | Hex 00 00 = DHCP Disable Hex 00 01 = DHCP Enable | X
MAC address | - | - | 28673 | 7001 | 3 | U48 | H'03' | Example: "1C-01-02-03-04-19" : Hex 1C 01 02 03 04 19 | X
Configured IP | - | - | 28676 | 7004 | 2 | U32 | H'03' | Example: "192.168.0.20" : Hex C0 A8 00 14 | X
Configured Netmask | - | - | 28678 | 7006 | 2 | U32 | H'03' | Example: "255.255.255.0" : Hex FF FF FF 00 | X
Configured DNS1 | - | - | 28680 | 7008 | 2 | U32 | H'03' | Example: "8.8.8.8": Hex 08 08 08 08 | X
Configured DNS2 | - | - | 28682 | 700A | 2 | U32 | H'03' | Example: "8.8.4.4": Hex 08 08 04 04 | X
Configured Gateway | - | - | 28684 | 700C | 2 | U32 | H'03' | Example : "192.168.0.1": Hex C0 A8 00 01 | X
Time Source | - | - | 28686 | 700E | 1 | U16 | H'03' | Hex 00 00 = NTP Hex 00 01 = Modbus | X
NTP server | - | - | 28687 | 700F | 16 | STRING | H'03' | Example : "pool.ntp.org" | X
TLS Mode | - | - | 28703 | 701F | 1 | U16 | H'03' | Hex 00 00 = Anonymous TLS Hex 00 01 = Cyphered TLS Hex 00 02 = Cyphered and Authenticated TLS | X
Factory Certificate Use | - | - | 28704 | 7020 | 1 | U16 | H'03' | Hex 00 00 = Use Certificat uploaded Hex 00 01 = Use default certificat | X
TCP Port Secure | - | 1 | 28705 | 7021 | 1 | U16 | H'03' | Example 802 : Hex 03 22 | X
TCP Port Unsecure | - | 1 | 28706 | 7022 | 1 | U16 | H'03' | Example 502 : Hex 01 F6 | X
DHCP Status | - | - | 28928 | 7100 | 1 | U16 | H'03' | Hex 00 00 = No error Hex 00 01 = An error occurs | X
RTC Status | - | - | 28929 | 7101 | 1 | U16 | H'03' | Hex 00 00 = RTC synchronized Hex 00 01 => RTC not synchronized | X
IP | - | - | 28930 | 7102 | 2 | U32 | H'03' | Example: "192.168.0.20" : Hex C0 A8 00 14 | X
Netmask | - | - | 28932 | 7104 | 2 | U32 | H'03' | Example: "255.255.255.0" : Hex FF FF FF 00 | X
DNS1 | - | - | 28934 | 7106 | 2 | U32 | H'03' | Example: "8.8.8.8": Hex 08 08 08 08 | X
DNS2 | - | - | 28936 | 7108 | 2 | U32 | H'03' | Example: "8.8.4.4": Hex 08 08 04 04 | X
Gateway | - | - | 28938 | 710A | 2 | U32 | H'03' | Example : "192.168.0.1": Hex C0 A8 00 01 | X
Radio Channel | - | 1 | 29184 | 7200 | 1 | U16 | H'03' | Radio channel 11 15 20 25 Example : 20 : Hex 00 14 | X
Number Of Commisioned Devices | - | 1 | 29185 | 7201 | 1 | U16 | H'03' | Example : 2 DPD connected : Hex 00 02 | X
RTU Enable | - | - | 29440 | 7300 | 1 | U16 | H'03' | Hex 00 00 = RTU Disable Hex 00 01 = RTU Enable | X
RTU Baud Rate | - | 1 | 29441 | 7301 | 2 | U32 | H'03' | 1200, 2400, 4800, 9600, 14400, 19200, 28800, 38400, 57600, 76800, 115200 Example: 115200: Hex 00 01 C2 00 | X
RTU parity | - | - | 29443 | 7303 | 1 | U16 | H'03' | Hex 00 00 = None Hex 00 01 = Even Hex 00 02 = Odd | X
RTU stop bit | - | 1 | 29444 | 7304 | 1 | U16 | H'03' | Example : 1 : Hex 00 01 | X
RTU Retry number | - | 1 | 29445 | 7305 | 1 | U16 | H'03' | Example : 3 : Hex 00 03 | X
RTU Timeout | ms | 1 | 29446 | 7306 | 1 | U16 | H'03' | Example : 1500ms : Hex 05 DC | X
Device name | - | - | 28672 | 7000 | 16 | STRING | H'03' | Example : Q1 |  | X | X
Device Appliance | - | - | 28688 | 7010 | 1 | U16 | H'03' | Hex 00 00 = Socket Hex 00 01 = Light Hex 00 02 = Fridge Hex 00 03 = Freezer Hex 00 04 = Air conditionner Hex 00 05 = Ventilation Hex 00 06 = Electronic appliance Hex 00 07 = Pump Hex 00 08 = Heating Zone Hex 00 09 = Floor heater Hex 00 0A = Charging socket Hex 00 0B = EVSocket Hex 00 0C = Oven Hex 00 0D = Kitchen appliance Hex 00 0E = Custom |  | X | X
Protection Curve | - | - | 28691 | 7013 | 1 | U16 | H'03' | Hex 00 00 = B Hex 00 00 = C |  | X | X
Current Rating | A | 0.5 | 28692 | 7014 | 1 | U16 | H'03' | Example : 16A : Hex 00 20 |  | X | X
Overload threshold (Ir) | A | 0.5 | 28693 | 7015 | 1 | U16 | H'03' | Example : 10A : Hex 00 14 |  | X | X
Overload delay | ms | 1 | 28694 | 7016 | 1 | U16 | H'03' | Example : 350ms : Hex 01 5E |  | X | X
Short Circuit Threshold Factor | - | 0.1 | 28695 | 7017 | 1 | U16 | H'03' | Example : 4.0 : Hex 00 28 |  | X | X
Short Circuit Threshold | A | 0.25 | 28696 | 7018 | 1 | U16 | H'03' | Example : 40A : Hex 00 A0 |  | X | X
RCD Threshold | mA | 1 | 28698 | 701A | 1 | U16 | H'03' | 30mA, 100mA Example: 30mA : Hex 00 1E |  | X | X
RCD type | - | - | 28699 | 701B | 1 | U16 | H'03' | Hex 00 01 = A Hex 00 02 = F |  | X | X
TrippingMode | - | - | 28709 | 7025 | 2 | U32 | H'03' | Mode on 32 bits. Value 0: Trip to OFF; Value 1 : Trip to Standby bit 0 = Overload protection bit 1 = Instantaneous protection bit 2 = Reserved bit 3 = RCD protection bit 4 = AFD protection bit 5-31 = reserved |  | X | X
Active protection | - | - | 28711 | 7027 | 2 | U32 | H'03' | Status on 32 bits. Value 0: Disabled; Value 1 : Enabled bit 0 = Overload protection bit 1 = Instantaneous protection bit 2 = Reserved bit 3 = RCD protection bit 4 = AFD protection bit 5-31 = reserved |  | X | X
RCM alarm Enable | - | - | 29454 | 730E | 1 | U16 | H'03' | Hex 00 00 = Disabled Hex 00 01 = Enabled
RCM alarm Threshold | mA | 1 | 29455 | 730F | 1 | U16 | H'03' | 30mA, 100mA Example: 30mA : Hex 00 1E
RCM alarm type | - | - | 29456 | 7310 | 1 | U16 | H'03' | Hex 00 01 = A Hex 00 02 = F

## Indicators
Indicators
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Last Trip Cause identification | - | - | 28960 | 7120 | 1 | U16 | H'03' | Hex 00 00 = No TRIP Hex 00 01 = Trip on overload Hex 00 02 = Trip on short circuit Hex 00 03 = Trip on short circuit Hex 00 04 = Trip on residual current Hex 00 05 = Trip on RCD test Hex 00 06 = Trip on arc fault Hex 00 07 = Trip on self test |  | X | X
Last Trip Cause date and time | s | 1 | 28961 | 7121 | 2 | U32 | H'03' | Time in second since 1st January 2000 |  | X | X
Transparent RCD test status | - | - | 28975 | 712F | 1 | U16 | H'03' | Hex 00 00 = No test performed Hex 00 01 = Success Hex 00 02 = Failed |  | X | X
Transparent RCD test date and time | s | 1 | 28976 | 7130 | 2 | U32 | H'03' | Time in second since 1st January 2000 |  | X | X
RCD test status | - | - | 28978 | 7132 | 1 | U16 | H'03' | Hex 00 00 = No test performed Hex 00 01 = Success Hex 00 02 = Failed |  | X | X
RCD test date and time | s | 1 | 28979 | 7133 | 2 | U32 | H'03' | Time in second since 1st January 2000 |  | X | X
Alarm statuses | - | - | 29440 | 7300 | 2 | U32 | H'03' | Statuses on 32 bits. Value 0: Inactive; Value 1 : Active bit 0-7 = reserved bit 8 = RCM alarm bit 9-31 = reserved |  | X | X
Product State | - | - | B803 | 47107 | 1 | U16 | H'03' | Hex 00 00 = OFF Hex 00 01 = Standby Hex 00 02 = ON |  | X | X

## Measuring
Mesuring
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
AC Frequency | Hz | 0.01 | 32768 | 8000 | 1 | U16 | H'03' | Example: 50,1Hz : Hex 13 92 |  | X | X
Differential current (RCM) | mA | 1 | 32777 | 8009 | 1 | U16 | H'03' | Example: 2mA : Hex 00 02 |  | X | X
PhA - RMS Voltage | V | 1 | 34816 | 8800 | 1 | U16 | H'03' | Example: 231V : Hex 00 E7 |  | X | X
PhA - RMS Current | A | 0.001 | 34819 | 8803 | 1 | U16 | H'03' | Example: 10,21A : Hex 27 E2 |  | X | X
PhA - Active Power | W | 1 | 34822 | 8806 | 1 | S16 | H'03' | Example: 2932W : Hex 0B 74 |  | X | X
PhA - Reactive Power | VAr | 1 | 34825 | 8809 | 1 | S16 | H'03' | Example: 122VAr : Hex 00 7A |  | X | X
PhA - Apparent Power | VA | 1 | 34828 | 880C | 1 | U16 | H'03' | Example: 3102VA : Hex 0C 1E |  | X | X
Active energy imported (Ea+) | Wh | 1 | 40962 | A002 | 4 | U64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80 |  | X | X
Active energy exported (Ea-) | Wh | 1 | 40966 | A006 | 4 | U64 | H'03' | Example: 36592000Wh: Hex 00 00 00 00 02 2E 59 80 |  | X | X
Reactive energy imported (Er+) | varh | 1 | 40970 | A00A | 4 | U64 | H'03' | Example: 56984000VArh: Hex 00 00 00 00 03 65 81 C0 |  | X | X
Reactive energy exported (Er-) | varh | 1 | 40974 | A00E | 4 | U64 | H'03' | Example: 56984000VArh: Hex 00 00 00 00 03 65 81 C0 |  | X | X
Apparent energy (Es) | VAh | 1 | 40978 | A012 | 4 | U64 | H'03' | Example: 68713000VAh: Hex 00 00 00 00 04 18 7A 28 |  | X | X

## Commands
Commands
Warning: All registers of a command request shall be sent in single Modbus request.
It is not possible to send it register per register
Command Reboot
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex : 00 00 |  | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 |  | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 00 |  | X | X
Parameters | - | - | 5393 | 1511 | 1 | U16 | H'16 | Hex 00 00 |  | X | X
Command identification
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex 00 02 | X | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 | X | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 02 | X | X | X
Parameters | - | - | 5393 | 1511 | 1 | U16 | H'16 | Identification time in secondes. Example: 15s: Hex 00 0F | X | X | X
Command Set time
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex 00 0A | X | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 | X | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 04 | X | X | X
Parameters | - | - | 5393 | 1511 | 2 | U16 | H'16 | Time in second since 1st January 2000 Example: 15185478s: Hex 00 E7 B6 46 | X | X | X
Command RCD test
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex 00 6D |  | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 |  | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 02 |  | X | X
Parameters | - | - | 5393 | 1511 | 1 | U16 | H'16 | Hex 00 00 = RCD test Hex 00 01 = Transparent RCD test |  | X | X
Command Acknowledge last trip cause
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex : 00 6E |  | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 |  | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 00 |  | X | X
Parameters | - | - | 5393 | 1511 | 1 | U16 | H'16 | Hex 00 00 |  | X | X
Command Set product state
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Command code | - | - | 5376 | 1500 | 1 | U16 | H'16 | Hex : 00 74 |  | X | X
Reserved | - | - | 5377 | 1501 | 15 | U16 | H'16 | All registers to Hex 00 00 |  | X | X
Length of parameters | - | - | 5392 | 1510 | 1 | U16 | H'16 | Hex 00 01 |  | X | X
Parameters | - | - | 5393 | 1511 | 1 | U16 | H'16 | Hex 00 00 = OFF Hex 00 01 = Standby Hex 00 02 = On |  | X | X
Command Result
Description | Unit | Resolution | Address DEC | Address HEX | Length (word) | Data Type | Function | Further information | TMF100 | AXX516D | AXF516D
Last command code | - | - | 5632 | 1600 | 1 | U16 | H'03' | Command code executed | X | X | X
Command status | - | - | 5633 | 1601 | 1 | U16 | H'03' | Hex 00 00 = Success Hex 00 01 = Command in progress Hex 00 02 = Busy, another command is already in progress Hex 00 03 = Unexpected error Hex 00 80 = Command not supported Hex 00 83 = Wrong number of parameters Hex 00 84 = Wrong parameter(s) value(s) Hex 00 86 = Wrong frame format request Hex 00 A0 = Slave not reachable Hex 00 A1 = Slave not commissioned | X | X | X